## IO_LIST
|  |  |  | Project n° | Project n° | Unit | Document code | Material Code | Serial n° | Rev. | Page
|  |  |  | 214359C | 214359C | 6602 | NM | 1551 | 0001 | 3F | Page 07 of 11
FRACTIONATION - INSTRUMENT LIST
ISBL (TEN )/ OSBL (ARTELIA) SCOPE |  | ISBL | ISBL | ISBL |  | ISBL | ISBL | ISBL | ISBL | ISBL | ISBL |  |  | ISBL | ISBL |  | ISBL | ISBL | ISBL | ISBL | OSBL | ISBL | ISBL | ISBL | ISBL | ISBL | OSBL | ISBL | ISBL | ISBL | ISBL | ISBL |  | ISBL |  | ISBL | ISBL | ISBL | ISBL | [5 empty] | ISBL | N/A | ISBL | ISBL | ISBL | ISBL | N/A | ISBL | ISBL | N/A | ISBL | ISBL | ISBL | ISBL | RP | RP | ISBL | ISBL | RP/INSP | RP/INSP | RP/INSP |  |  |  |  | ISBL | ISBL | ISBL | ISBL | ISBL | ISBL |  | ISBL | [6 empty] | ISBL | ISBL | ISBL | ISBL | ISBL |  |  |  |  | OSBL | ISBL | ISBL | ISBL/OSBL |  | ISBL | OSBL | ISBL/OSBL | OSBL | OSBL | OSBL | OSBL | OSBL | ISBL | ISBL | ISBL | ISBL | OSBL | ISBL/OSBL |  |  | ISBL |  |  |  |  | ISBL | ISBL | ISBL | ISBL | ISBL | ISBL |  |  |  |  | ISBL | ISBL | ISBL | ISBL | RP/INSP | ISBL | ISBL | ISBL | ISBL | [7 empty] | ISBL | [9 empty] | OSBL | OSBL | OSBL | OSBL | OSBL | OSBL | OSBL | OSBL | OSBL | OSBL | OSBL | OSBL | OSBL | OSBL | OSBL | OSBL | OSBL |  |  |  | ISBL | ISBL
Doc_Revision to be applied |  | IFD1 | IFD1 | IFD1 | N/A | IFD1 | IFD2 | IFD1 | IFD1 | IFD1 | IFD1 | N/A | N/A | IFD1 | IFD1 | N/A | IFD1 | IFD1 | IFD1 | IFD1 | N/A | IFD2 | IFD2 | IFD3 | IFD2 | IFD1 | N/A | N/A | N/A |  | IFD1 | IFD1 |  | IFD1 (Chk by Nohora) |  | IFD1 | IFD2 | IFD1 | IFD1 | [5 empty] | IFD3 |  | IFD3 | IFD3 | IFD3 | IFD3 |  | IFD3 |  | IFD3 | IFD3 | IFD3 | IFD3 | IFD3 by SIL Man | N/A | N/A | IFD3 by SIL Man | IFD3 by SIL Man | N/A | N/A | N/A | N/A | N/A | N/A | N/A | IFD1 chk by EDG | IFD1 chk by EDG | IFD1 chk by EDG | IFD1 chk by EDG | IFD1 chk by EDG | IFD1 chk by EDG |  | IFD2 | [6 empty] | IFD2 | IFD2 | IFD2 | IFD2 | IFD2 | N/A | N/A | N/A | N/A | N/A | IFD1 | IFD1 | IFD1 | N/A | IFD1 | N/A | IFD2 | N/A | N/A | N/A | N/A | N/A | IFD2 |  | IFD2 | IFD3 | N/A | IFD2 | N/A | N/A | IFD3 | N/A | N/A | N/A |  | IFD2 | IFD2 | IFD2 | IFD2 | IFD2 | IFD2 | N/A | N/A | N/A | N/A | IFD3 - Only aplycable for Safety On-Off Valves with Air Tank |  |  |  | N/A | IFD2 | IFD2 | IFD2 | IFD2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | IFD2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | IFD3 | IFD3
| N° typical loop | 214359C-000-PID-0090-000x |  |  | Desciption typical loop | REV | Id. | TAG | OLD_TAG | SERVICE | FUNCTION | FUNCTION | SPI Process_Function | SUB_FUNCTION | METROLOG | METROLOG_DB_REF | LOC | NAME_LOC | LOOP_TYPE | SYSTEM | NUM | RANGE_MIN | RANGE_MAX | THRES_VALUE | RANGE & THRES. UNIT | PID | OPERGRAPH | CONT_DIAGRAM (9R) | LOGIG_DIAGRAM (9S) | FUNC_LOOP | PLANT UNIT | OBS_GEN | OBS_RAF | ANALYSER_TYPE | FUT_SPEC_03 | RG | LOOP | MOD | MOD_OBS | OBS_PRJ | FUT_SPEC_04 | FUT_SPEC_05 | FUT_SPEC_06 | TIE-IN | DOC_HAZOP | DOC_SIL | DOC_SIF | SIF_1 | SIF_X | SIL_LEVEL | AIL_LEVEL | FALLBACK_POSITION | FAIL POSITION SPI | FAILSAFE | SRC | SRC_DESC | S_TYPE | PST | TEST_PROC_NUMBER | TEST_TYPE | T1 | MTTR | COCL | COCL_DESC | COCL_VALUE | OBS_SIS | FUT_SPEC_07 | FUT_SPEC_08 | FUT_SPEC_09 | HOOK_UP | INS | HEAT | HEAT_TYPE | INSULATION | HEAT_INSULATION_STD | BUFFER_LIQ | CAL_MIN_EQU | UN_CAL_MIN | UN_CAL_MIN_FLAG | CAL_MAX_EQU | UN_CAL_MAX | UN_CAL_MAX_FLAG | REG_MIN_EQU | UN_REG_MIN | UN_REG_MIN_FLAG | REG_MAX_EQU | UN_REG_MAX | UN_REG_MAX_FLAG | GPS | ACC | OBS_INS | FUT_SPEC_12 | SEND_TO | SIG | ALIM | ISOLATOR | LIGHTNING | DUPLICATOR | I/O_CARD_TYPE | MARSH_CABINET | SYSTEM_CABINET | SEC | RACK | SLOT | I/O_ADDRESS | JB_TAG | JB_SPI_TAG | ELECTRICAL_H-UP | AIR_MANIFOLD | LOOP_DWG | JB_DWG | NET_TYPE | NET_DB_REF | OBS_WIR | FUT_SPEC_13 | FUT_SPEC_14 | FUT_SPEC_15 | LINE NUMBER | FLUID | LGS | P_SER | P_MAX | T_SER | T_MAX | OBS_PRO | FUT_SPEC_16 | FUT_SPEC_17 | FUT_SPEC_18 | PED | VOL_PED | PED_CAT | PED_MODULE | PED_SAFE_EQU | A_C_S | ATEX_ZONE | ATEX_GAS_ZONE | ATEX_TEMP_ZONE | ATEX_CERT | ATEX_CE_NUMBER | DOC_ATEX | OBS_REG | FUT_SPEC_19 | FUT_SPEC_20 | FUT_SPEC_21 | DATA_SHEET | DATE_SERV | CTG_CODE | SAP_LINK | PLANT_NUMBER | SECTION_RAF | OBS_SUP | FUT_SPEC_22 | FUT_SPEC_23 | FUT_SPEC_24 | PRIORITY | BYP | AL_ACT | AL_IND | AL_EQUA | DESC_AL_EQUA | BUNDLED | MSK_GSD | MSK_SD | MSK_EQUIP | MSK_START | MSK_PERTU | MSK_AL_EQUA | DESC_MSK_AL_EQUA | MSK_1DEF | ALARM_REM | OBS_ALA | FUT_SPEC_25 | FUT_SPEC_26 | FUT_SPEC_27 | "0" Word | "1" Word | RAF_01 | RAF_02 | RAF_03 | RAF_04 | RAF_05 | RAF_06 | RAF_07 | RAF_08 | RAF_09 | RAF_10 | RAF_11 | RAF_12 | RAF_13 | RAF_14 | RAF_15 | RAF_16 | RAF_17 | RAF_18 | RAF_19 | RAF_20 | RAF_21 | RAF_22 | RAF_23 | RAF_24 | RAF_25 | RAF_26 | RAF_27 | RAF_28 | RAF_29 | RAF_30 | RAF_31 | RAF_32 | RAF_33 | RAF_34 | RAF_35 | RAF_36 | RAF_37 | RAF_38 | RAF_39 | RAF_40 | PROJ_01 | PROJ_02 | PROJ_03 | PROJ_04 | PROJ_05 | PROJ_06 | PROJ_07 | PROJ_08 | PROJ_09 | PROJ_10 | PROJ_11 | PROJ_12 | PROJ_13 | PROJ_14 | PROJ_15 | PROJ_16 | PROJ_17 | PROJ_18 | PROJ_19 | PROJ_20 | PROJ_21 | PROJ_22 | PROJ_23 | PROJ_24
| Only for DB Typical | Valves & Motor typical GALAXIE Project (include in PID Legend) | Typical Control Schema GALAXIE Project | SPI Internal Loop Order GALAXIE Project | Only for DB Typical | [5 empty] | EN | FR | DE | EN | Y/N | File name | [7 empty] | CHECK SEUIL and ALARM EQUAL |  | File name | File name | File name | File name |  |  | Spare Observation if necessary | Spare Observation if necessary | [5 empty] | Spare Observation if necessary | Spare Observation if necessary |  |  |  |  | File name | File name | File name | [5 empty] | FIELD T.EN For Internal Checking | Y/N or empty |  |  |  |  | File name |  | - | - | Y/N or black |  |  | Spare Observation if necessary |  |  |  | File name |  |  |  |  | File name | [15 empty] | Spare Observation if necessary | [15 empty] | T.EN for Internal Checking | T-ELECTR H-UP |  | File name | File name |  | File name | [19 empty] | Y/N or empty | [7 empty] | Spare Observation if necessary | [9 empty] | Spare Observation if necessary | [10 empty] | Y/N or empty | Y/N or empty | [7 empty] | Spare Observation if necessary |  |  |  | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary
[5 empty] | Description Ligne Desciption typical loop | Revision index of each record | Internal Id. SPI or AVEVA | TAG number of the function or equipment | Old TAG number | Service of the function or equipment | Type of equipment or function handled | Type of equipment or function handled |  | Sub function of the type of equipment. | Indicate if the equpment or processing system are tracked metrologically | Gives the name of the system database managing the metrological traking for equipment. | Location of the equipment or of the function handled | Common name for all locations | Loop type (control / safety / Maintenance) | System type of the processing system managing the function or equipment | Assigns a serial number to the processing system managing the function or equipment | Bottom value of display scale | Top value of the display scale | Threshold setting value | Unit of the display scale or physical unit | Number of the PID of the function or equipment | Number of the opergraph of the function or equipment | Control drawing number | Number of the safety or automation logic diagram | Functional loop name | Unit Name | Observations associated with the general fields | Observations | Analyser Type | Spare for specification GS RC INS 107 | Serial number of the record in the loop | Loop name | Modification type on instrument | Observations associated with the modification | Observations | Spare for specification GS RC INS 107 | Spare for specification GS RC INS 107 | Spare for specification GS RC INS 107 |  | HAZOP review document number (G-HSEQ-908) | SIL review document number (G-HSEQ-908) | SIF review document number (GS RC INS 150) | Assignment in the safety instrumented functions (GS RC INS 107 / GS RC INS 150) | Assignment in the safety instrumented functions (GS RC INS 107 / GS RC INS 150) | Integrity level of the equipment SIL (GS RC INS 600) | Integrity level of the equipment AIL (GS RC INS 600) | Fallback position for measuring instrument in case of his failure (GS RC INS 400) |  | Defines whether the equipment has a FAILSAFE mode (GS RC INS 400 / GS RC INS 450 / GS RC INS 451) | Safety regulation classification of the sensor or actuator depending country | Description of the SRC service | Origin of safety function covered (GS RC INS 100) | Process Safety Time (GS RC INS 451) | Safety test procedure for the function or equipment | Particular physical test device for the equipment | T1 (GS RC INS 600) | MTTR (GS RC INS 600) | Limit critical operating conditions | Description of the limit critical operating conditions | Physical values of the limit critical operating conditions | Observations associated with the safety fields | Spare for specification GS RC INS 107 | Spare for specification GS RC INS 107 | Spare for specification GS RC INS 107 | 1 | Instrument piping class (GS RC INS 200) | Instrument heat tracing type (GS RC INS 220) | Instrument heat tracing fluid (GS RC INS 220) | Instrument insulating type (GS RC INS 220) | Number of standard protection diagram (GS RC INS 220) | Type of buffer liquid between the sensor and the process fluid (GS RC INS 400) | Minimum instrument calibration range | Unit instrument calibration range | Minimum Instrument setting | Maximum instrument calibration range | Unit instrument calibration range | Maximum Instrument setting | Minimum instrument range | Unit instrument range | unit for the instrument | Maximum Instrument setting | Unit instrument range | Maximum Instrument setting | Geographic coordinates of the instrument (GS RC INS 150) | Instrument access means (GS RC INS 200) | Observations associated with the installation fields | Spare for specification GS RC INS 107 | Gives the end point for a link between systems | Nature of the signal for the inputs/outputs of an electrical/electronic/programmable electronic system or for exchanges between systems (GS RC INS 300 / GS RC INS 520 / GS RC INS 530) | Loop power supply (GS RC INS 300 / GS RC INS 520 / GS RC INS 530) | Type of isolator (GS RC INS 300 / GS RC INS 520 / GS RC INS 530) | Connection of a Lightning arrester to the instrument (GS RC INS 301) | Connection to signal duplicator (GS RC INS 810) | Type of I/O card where is linked the signal (GS RC INS 520 / GS RC INS 530) | Number of the connection cabinet for the instrument multicable (GS RC INS 105 / GS RC INS 300) | Number of the system cabinet (BPCS or SIS) where is linked the instrument (GS RC INS 105) | Assignment of the functional group in the oil unit or processing section in the digital control system | Number of the rack or face plate where is linked the instrument | Number of the rack or face plate where is linked the instrument | Number of the rack or face plate where is linked the instrument | Identifier of the junction box where is linked the instrument (GS RC INS 300 / GS RC INS 105) |  | Define the electrical material for Field Wiring | Identifier of the air distrubutor where is linked the instrument | Number of the loop drawing or troubleshooting drawing (GS RC INS 300 / GS RC INS 150) | Junction box drawing number (GS RC INS 300 / GS RC INS 150) | Gives the type of field bus network wired or wireless for the instrument | Gives the name of the system database managing the user network | Observations associated with the wirered fields | Spare for specification GS RC INS 107 | Spare for specification GS RC INS 107 | Spare for specification GS RC INS 107 |  | Fluid family in contact with the instrument (GS RC INS 200 / RG RC PVA 102) | State of the fluid in contact with the instrument (GS RC INS 107) | Pression de service du fluide (GS RC INS 107) | Pression maxi de service du fluide (GS RC INS 107) | Fluid operating temperature (GS RC INS 107) | Fluid Max operating temperature (GS RC INS 107) | Observations associated with the process fields | Spare for specification GS RC INS 107 | Spare for specification GS RC INS 107 | Spare for specification GS RC INS 107 | Spare for specification GS RC INS 107 | Volume of PED pressure chamber | PED category module | PED category module | PED safety accessory | Area Classification Standard. Standard or code classification for explosive atmosphere area | Type of ATEX ZONE where the instrument is located | ATEX gas group of the zone where the instrument is located | The most restrictive temperature class of the zone where the instrument is located | ATEX certificate of the instrument | Number of certificate of conformity | ATEX review document number | Observations associated with the regulatory fields | Spare for specification GS RC INS 107 | Spare for specification GS RC INS 107 | Spare for specification GS RC INS 107 | Number of the data sheet | Instrument start-up date | Instrument start-up date (DIGGR1600INS005) | SAP link for the instrument. | Instument code of the unit in the Refinery. | Section number of the refinery. | Observations associated with the supplier fields | Spare for specification GS RC INS 107 | Spare for specification GS RC INS 107 | Spare for specification GS RC INS 107 | Alarm priority (GS RC INS 502) | Type of maintenance bypass function associated with the alarm (GS RC INS 502) | Procedure to be followed to treat the alarm (GS RC INS 502) | Procedure to be followed when the alarm is unavailable (GS RC INS 502) | Equation generating the alarm (GS RC INS 502) | Equation description generating the alarm (GS RC INS 502) | Alarm group to which the alarm belongs (GS RC INS 502) | Assignment of the general shutdown masking for the alarm (GS RC INS 502) | Assignment of the unit shutdown masking for the alarm (GS RC INS 502) | Assignment of the equipment masking on shutdown for the alarm (GS RC INS 502) | Assignment of the unit start up masking for the alarm (GS RC INS 502) | Assignment of the unit disturbed operation masking for the alarm (GS RC INS 502) | Individual masking equation of the alarm (GS RC INS 502) | Equation description of the individual masking alarming (GS RC INS 502) | Assignment of the first fault masking for the alarm (GS RC INS 502) | Observations associated with the alarm (GS RC INS 502) | Observations associated with the alarm fields | Spare for specification GS RC INS 107 | Spare for specification GS RC INS 107 | Spare for specification GS RC INS 107 |  |  | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use
- | - | - | - | 0 | - | 1 | - | 660H2_S_5901 | - | 660-2 GAS DETECTOR (H2) | GAS DETECTOR H2 | - | - | 3 WIRES | N | - | L | ST1B | SIS | S-PLC-FGS | - | 0 | 100 | - | % LEL | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 3 | 660H25901 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI50 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJGS532/T01 | - | E11203 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | 660H2_S_5902 | - | 660-2 GAS DETECTOR (H2) | GAS DETECTOR H2 | - | - | 3 WIRES | N | - | L | ST1B | SIS | S-PLC-FGS | - | 0 | 100 | - | % LEL | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 3 | 660H25902 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI50 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJGS532/T02 | - | E11203 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660HC_S_1901 | - | 660-1 GAS DETECTOR(HC) | GAS DETECTOR HC | - | - | 3 WIRES | N | - | L | ST1B | SIS | S-PLC-FGS | - | 0 | 100 | - | % LEL | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 3 | 660HC1901 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI50 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJGS103/T01 | - | E11203 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | 660HC_S_5910 | - | 660-2 GAS DETECTOR(HC) | GAS DETECTOR HC | - | - | 3 WIRES | N | - | L | ST1B | SIS | S-PLC-FGS | - | 0 | 100 | - | % LEL | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 3 | 660HC5910 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI50 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJGS532/T03 | - | E11203 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | 660HC_S_5901 | - | 660-2 GAS DETECTOR(HC) | GAS DETECTOR HC | - | - | 3 WIRES | N | - | L | ST1B | SIS | S-PLC-FGS | - | 0 | 100 | - | % LEL | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 3 | 660HC5901 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI50 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJGS530/T01 | - | E11203 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | 660HC_S_5902 | - | 660-2 GAS DETECTOR(HC) | GAS DETECTOR HC | - | - | 3 WIRES | N | - | L | ST1B | SIS | S-PLC-FGS | - | 0 | 100 | - | % LEL | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 3 | 660HC5902 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI50 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJGS530/T02 | - | E11203 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | 660HC_S_5903 | - | 660-2 GAS DETECTOR(HC) | GAS DETECTOR HC | - | - | 3 WIRES | N | - | L | ST1B | SIS | S-PLC-FGS | - | 0 | 100 | - | % LEL | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 3 | 660HC5903 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI50 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJGS530/T03 | - | E11203 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | 660HC_S_5904 | - | 660-2 GAS DETECTOR(HC) | GAS DETECTOR HC | - | - | 3 WIRES | N | - | L | ST1B | SIS | S-PLC-FGS | - | 0 | 100 | - | % LEL | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 3 | 660HC5904 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI50 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJGS530/T04 | - | E11203 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | 660HC_S_5906 | - | 660-2 GAS DETECTOR(HC) | GAS DETECTOR HC | - | - | 3 WIRES | N | - | L | ST1B | SIS | S-PLC-FGS | - | 0 | 100 | - | % LEL | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 3 | 660HC5906 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI50 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJGS531/T01 | - | E11203 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | 660HC_S_5907 | - | 660-2 GAS DETECTOR(HC) | GAS DETECTOR HC | - | - | 3 WIRES | N | - | L | ST1B | SIS | S-PLC-FGS | - | 0 | 100 | - | % LEL | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 3 | 660HC5907 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI50 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJGS531/T02 | - | E11203 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660NTH_S_5901 | - | 660-2 FLAME DETECTOR FOR (HC) | FLAME DETECTOR | - | - | 3 WIRES | N | - | L | ST1B | SIS | S-PLC-FGS | - | 0 | 100 | - | % LEL | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 3 | 660NH5901 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI50 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJGS532/T04 | - | E11203 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660NTH_S_5902 | - | 660-2 FLAME DETECTOR FOR (HC) | FLAME DETECTOR | - | - | 3 WIRES | N | - | L | ST1B | SIS | S-PLC-FGS | - | 0 | 100 | - | % LEL | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 3 | 660NH5902 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI50 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJGS532/T05 | - | E11203 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | 660HC_S_5911 | - | 660-2 GAS DETECTOR(HC) | GAS DETECTOR HC | - | - | 3 WIRES | N | - | L | ST1B | SIS | S-PLC-FGS | - | 0 | 100 | - | % LEL | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 3 | 660HC5911 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI50 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJGS531/T03 | - | E11203 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | 660HC_S_5912 | - | 660-2 GAS DETECTOR(HC) | GAS DETECTOR HC | - | - | 3 WIRES | N | - | L | ST1B | SIS | S-PLC-FGS | - | 0 | 100 | - | % LEL | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 3 | 660HC5912 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI50 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJGS530/T06 | - | E11203 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | 660HC_S_5913 | - | 660-2 GAS DETECTOR(HC) | GAS DETECTOR HC | - | - | 3 WIRES | N | - | L | ST1B | SIS | S-PLC-FGS | - | 0 | 100 | - | % LEL | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 3 | 660HC5913 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI50 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJGS530/T07 | - | E11203 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660NTH2_S_5901 | - | 660-2 FLAME DETECTOR FOR (H2) | FLAME DETECTOR | - | - | 3 WIRES | N | - | L | ST1B | SIS | S-PLC-FGS | - | 0 | 100 | - | % LEL | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 3 | 660NH25901 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI50 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJGS532/T06 | - | E11203 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660NTH2_S_5902 | - | 660-2 FLAME DETECTOR FOR (H2) | FLAME DETECTOR | - | - | 3 WIRES | N | - | L | ST1B | SIS | S-PLC-FGS | - | 0 | 100 | - | % LEL | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 3 | 660NH25902 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI50 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJGS532/T07 | - | E11203 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 2 | - | 660HC_5908 | - | 660-2 GAS DETECTOR(HC) | GAS DETECTOR HC | - | - | 3 WIRES | N | - | L | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 3 | 660HC5908 | C2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI50 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJGS532/T08 | - | E11203 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | 660HC_S_5909 | - | 660-2 GAS DETECTOR(HC) | GAS DETECTOR HC | - | - | 3 WIRES | N | - | L | ST1B | SIS | S-PLC-FGS | - | 0 | 100 | - | % LEL | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 3 | 660HC5909 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI50 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJGS532/T09 | - | E11203 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660NTC_S_1901 | - | 660-1 HEAT DETECTOR | HEAT DETECTOR | - | - | 4 wires | N | - | L | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 3 | 660NTC1901 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJGS102/P03 | - | E11204 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660NTC_S_5901 | - | 660-2 HEAT DETECTOR | HEAT DETECTOR | - | - | 4 wires | N | - | L | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 3 | 660NTC5901 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJGS500/P03 | - | E11204 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660NTC_S_5902 | - | 660-2 HEAT DETECTOR | HEAT DETECTOR | - | - | 4 wires | N | - | L | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 3 | 660NTC5902 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJGS500/P04 | - | E11204 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | 660HS_5932 | - | 660 - 2 REST ACKNOWLEDGE | HS - ACK | - | - | - | N | - | L | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 7 | 660H5902 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJGS500/P05 | - | E11204 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 2 | - | 660HC_5905 | - | 660-2 GAS DETECTOR(HC) | GAS DETECTOR HC | - | - | 3 WIRES | N | - | L | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 3 | 660HC5905 | C2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI50 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJGS530/T05 | - | E11203 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660HC_S_5500 | 660 HC_ 5500 | 660-2 GAS DETECTOR (HC) ON 660K5001 | GAS DETECTOR HC | - | - | - | - | - | L | ST1B | SIS | S-PLC-FGS | - | 0 | 100 | - | % LEL | 214359C-6602-PID-0021-0212 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 4 | 660HC5500 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | % LEL | - | 100 | % LEL | - | - | - | - | - | - | AI50 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJGS532/T10 | - | E11203 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660 HC_ 5500-SP
- | - | - | - | 3 | - | 1 | - | 660TT5330 | - | 660F5001 - 660TT5330 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | 0 | 900 | - | c | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5330 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660BJM537/P15 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TT5331 | - | 660-F-5001 | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 300 | - | °C | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5330 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-441 / PART 1 FOLIO 9 | - | NO | - | NI (NOT INSULATED) | - | - | 0 | °C | - | 900 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM537/P16 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | FG | OTHER | 0 | - | 846 | 866 | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5330-SP
- | - | - | - | 14 | - | 1 | - | 660TI5332 | - | 660F5001 COMBUSTION AIR PREHEATER | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | BPCS | DCS | - |  | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5331 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-441 / PART 1 FOLIO 9 | - | NO | - | NI (NOT INSULATED) | - | - | 0 | °C | - | 300 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM537/P17 | - | E10201 | - | - | - | - | - | - | - | - | - | DUCTS | FG | OTHER | -0.01 | 2.5 | 120 | 371 | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5331-SP
- | - | - | - | 0 | - | 1 | - | 660HS_5901 | - | 660-2 MANUAL CALL POINT(WEATHERPROOF) | PB | - | - | - | N | - | L | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 7 | 660H5901 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJGS500/P01 | - | E11204 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | 660HS_5902 | - | 660-2 MANUAL CALL POINT(WEATHERPROOF) | PB | - | - | - | N | - | L | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 7 | 660H5902 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJGS500/P02 | - | E11204 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660BE5370 | - | BURNER FLAME DETECTION ELEMENT | FLAME DETECTOR | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | LL | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | Alarm (LL) | - | - | - | 7 | 660B5370 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | EXT_24V | NR | - | - | - | - | - | - | - | - | - | 660BJMS505/P01 | - | E10212* | 660IADM510/09 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660BE5372 | - | BURNER FLAME DETECTION ELEMENT | FLAME DETECTOR | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | LL | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | Alarm (LL) | - | - | - | 7 | 660B5372 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | EXT_24V | NR | - | - | - | - | - | - | - | - | - | 660BJMS505/P02 | - | E10212* | 660IADM511/03 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660BE5374 | - | BURNER FLAME DETECTION ELEMENT | FLAME DETECTOR | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | LL | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | Alarm (LL) | - | - | - | 7 | 660B5374 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | EXT_24V | NR | - | - | - | - | - | - | - | - | - | 660BJMS505/P03 | - | E10212* | 660IADM511/04 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660BE5376 | - | BURNER FLAME DETECTION ELEMENT | FLAME DETECTOR | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | LL | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | Alarm (LL) | - | - | - | 7 | 660B5376 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | EXT_24V | NR | - | - | - | - | - | - | - | - | - | 660BJMS505/P04 | - | E10212* | 660IADM511/05 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- |  | MCC22 |  | 17 |  | 1 |  | 660XAH5102A | - | 660-EM-5002B VIBRATION | ALARM |  |  | - | - |  | CRD | SdC | BPCS/SIS | DCS | [5 empty] | 214359C-6602-PID-0021-0206 |  |  |  |  | 660-2-Fractionation | - |  | - |  | - | 660EM5002A | N | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [7 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [5 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- |  | MCC22 |  | 17 |  | 1 |  | 660XAH5102B | - | 660-EM-5002B VIBRATION | ALARM |  |  | - | - |  | CRD | SdC | BPCS/SIS | DCS | [5 empty] | 214359C-6602-PID-0021-0206 |  |  |  |  | 660-2-Fractionation | - |  | - |  | - | 660EM5002B | N | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [7 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [5 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- |  | MCC22 |  | 17 |  | 1 |  | 660XAH5006A | - | 660-EM-5006A VIBRATION | ALARM |  |  | - | - |  | CRD | SdC | BPCS/SIS | DCS | [5 empty] | 214359C-6602-PID-0021-0210 |  |  |  |  | 660-2-Fractionation | - |  | - |  | - | 660EM5006A | N | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [7 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [5 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- |  | MCC21 |  | 12 |  | 1 |  | 660XAH5006B | - | 660-EM-5006B VIBRATION | ALARM |  |  | - | - |  | CRD | SdC | BPCS/SIS | DCS | [5 empty] | 214359C-6602-PID-0021-0210 |  |  |  |  | 660-2-Fractionation | - |  | - |  | - | 660EM5006B | N | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [7 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [5 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- |  | MCC22 |  | 17 |  | 1 |  | 660XAH5006C | - | 660-EM-5006C VIBRATION | ALARM |  |  | - | - |  | CRD | SdC | BPCS/SIS | DCS | [5 empty] | 214359C-6602-PID-0021-0210 |  |  |  |  | 660-2-Fractionation | - |  | - |  | - | 660EM5006C | N | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [7 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [5 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- |  | MCC21 |  | 16 |  | 1 |  | 660XAH5006D | - | 660-EM-5006D VIBRATION | ALARM |  |  | - | - |  | CRD | SdC | BPCS/SIS | DCS | [5 empty] | 214359C-6602-PID-0021-0210 |  |  |  |  | 660-2-Fractionation | - |  | - |  | - | 660EM5006D | N | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [7 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [5 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  |  |  | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV15 | - | 8 | - | 1 | - | 660UYS5001F | - | On-ff Valve 660UVS5001 | AIR SOLENOID SPRING | - | - | SOLENOID ONLY | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS503/C01-C02 | - | E10207 | 660IADM518/05 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5001F-SP
- | - | UV05 | - | 7 | - | 1 | - | 660HS5011 | 660-HS -5011A | 660-UV-5011 | ESD PB | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5011 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS501/P01 | - | E10204 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV15 | - | 4 | - | 1 | - | 660UYS5001O | - | 660-UVS-5001 | AIR SOLENOID SPRING | - | - | SOLENOID ONLY | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS503/C03-C04 | - | E10207 | 660IADM518/05 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5001-SP
- | - | UV12 | - | 4 | - | 1 | - | 660HS5303 | 660-HS -5302 | 660-UVS-5302/5301 RESET | PB | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660H5303 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS506/P01 | - | E10204 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 2 | - | 660LI0005 | 660LIC0005 | DEBUTANIZER | INDICATION | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660L0005 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 2 | - | 660LSHH0005 | 660LAH0005 | DEBUTANIZER | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | SIS | S-PLC | - | - | - | Note:6 | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660L0005 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 2 | - | 660LTS0005 | 660LT0005 | DEBUTANIZER | PRESSURE DP | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | 0 | 100 | - | % | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660L0005 | M | - | - | - | - | - | TIP-660-5917-I | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-430 / PART 1 FOLIO 2 | Cl6 | - | - | - | - | - | -1736 | mmH2O 4°C | - | -708 | mmH2O 4°C | - | -10000 | mmH2O 4°C | - | 10000 | mmH2O 4°C | - | - | - | - | - | - | AI11 | INT | - | - | - | - | - | - | - | - | - | - | AQJBG (13,14) | - | E10201 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Phase:Gas / Group:1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- |  | - |  | 22 |  | 2 |  | 660LC0041 | - | DEBUTANIZER | CONTROLLER |  |  | - | - |  | CRD | SdC | BPCS/SIS | DCS | [5 empty] | 214359C-6602-PID-0021-0215 |  |  |  |  | 660-2-Fractionation | - |  | - | - | 4 | 660L0041 | N | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [5 empty] | - | - | - |  | - | - | [6 empty] | - |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 2 | - | 660LI0041AA | 660LI0041 | DEBUTANIZER | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660L0041 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- |  | - |  | 16 |  | 2 |  | 660LI0041BA | - | DEBUTANIZER | INDICATION |  |  | - | - |  | CRD | SdC | BPCS/SIS | DCS | [5 empty] | 214359C-6602-PID-0021-0215 |  |  |  |  | 660-2-Fractionation | - |  | - | - | 5 | 660L0041 | N | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [5 empty] | - | - | - |  | - | - | [6 empty] | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- |  | - |  | 17 |  | 2 |  | 660LI0041CA | - | DEBUTANIZER | INDICATION |  |  | - | - |  | CRD | SdC | BPCS/SIS | DCS | [5 empty] | 214359C-6602-PID-0021-0215 |  |  |  |  | 660-2-Fractionation | - |  | - | - | 5 | 660L0041 | N | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [5 empty] | - | - | - |  | - | - | [6 empty] | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 2 | - | 660LSHH0041A | 660LSHH0041 | DEBUTANIZER - 660LTS0041A | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - | - | - | High Aalarm (1790) High High Alamr (2540) | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660L0041 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- |  | - |  | 20 |  | 2 |  | 660LSHH0041B | - | DEBUTANIZER - 660LTS0041B | SOFT THRESHOLD |  |  | - | - |  | ITR | ST1D | BPCS/SIS | S-PLC |  |  |  | Low Alarm (1045) Low lOw Alarm (300) |  | 214359C-6602-PID-0021-0215 |  |  |  |  | 660-2-Fractionation | - |  | - | - | 7 | 660L0041 | N | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [5 empty] | - | - | - |  | - | - | [6 empty] | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- |  | - |  | 21 |  | 2 |  | 660LSHH0041C | - | DEBUTANIZER - 660LTS0041C | SOFT THRESHOLD |  |  | - | - |  | ITR | ST1D | BPCS/SIS | S-PLC |  |  |  | High Aalarm (1790) High High Alamr (2540) |  | 214359C-6602-PID-0021-0215 |  |  |  |  | 660-2-Fractionation | - |  | - | - | 7 | 660L0041 | N | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [5 empty] | - | - | - |  | - | - | [6 empty] | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 2 | - | 660LSLL0041A | 660LSLL0041 | DEBUTANIZER - 660LTS0041A | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - | - | - | Low Alarm (1045) Low lOw Alarm (300) | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660L0041 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- |  | - |  | 18 |  | 2 |  | 660LSLL0041B | - | DEBUTANIZER - 660LTS0041B | SOFT THRESHOLD |  |  | - | - |  | ITR | ST1D | BPCS/SIS | S-PLC |  |  |  | High Aalarm (1790) High High Alamr (2540) |  | 214359C-6602-PID-0021-0215 |  |  |  |  | 660-2-Fractionation | - |  | - | - | 7 | 660L0041 | N | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [5 empty] | - | - | - |  | - | - | [6 empty] | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- |  | - |  | 19 |  | 2 |  | 660LSLL0041C | - | DEBUTANIZER - 660LTS0041C | SOFT THRESHOLD |  |  | - | - |  | ITR | ST1D | BPCS/SIS | S-PLC |  |  |  | High Aalarm (1790) High High Alamr (2540) |  | 214359C-6602-PID-0021-0215 |  |  |  |  | 660-2-Fractionation | - |  | - | - | 7 | 660L0041 | N | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [5 empty] | - | - | - |  | - | - | [6 empty] | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 2 | - | 660LTS0041A | 660LTS0041 | DEBUTANIZER | PRESSURE DP | - | - | W/T SEAL+CAPILLARY | - | - | L | ST1D | BPCS/SIS | CONV | - | 150 | 2650 | - | mm | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660L0041 | R2D2 | - | - | - | - | - | TIP-660-5918-I | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-430 / PART 1 FOLIO 2 | CI6 | NO | - | NI (NOT INSULATED) | - | - | -1736 | mmH2O 4°C | - | -708 | mmH2O 4°C | - | -10000 | mmH2O 4°C | - | 10000 | mmH2O 4°C | - | - | - | - | - | - |  | INT | NR | - | - | - | - | - | - | - | - | - | AQJBG (11,12) | - | E10201 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Phase:Gas / Group:1 | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- |  | - |  | 10 |  | 2 |  | 660LTS0041AA | - | DEBUTANIZER | OUTPUT CONVERTER |  |  | - | - |  | ITR | ST1D | BPCS/SIS | S-PLC | [5 empty] | 214359C-6602-PID-0021-0215 |  |  |  |  | 660-2-Fractionation | - |  | - | - | 3 | 660L0041 | N | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [5 empty] | AI11 | INT | NR |  | - | - | [6 empty] | - |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- |  | - |  | 13 |  | 2 |  | 660LTS0041AB | - | DEBUTANIZER | OUTPUT CONVERTER |  |  | - | - |  | ITR | ST1C | BPCS/SIS | DCS | [5 empty] | 214359C-6602-PID-0021-0215 |  |  |  |  | 660-2-Fractionation | - |  | - | - | 3 | 660L0041 | N | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [5 empty] | AI11 | EXT | NR |  | - | - | [6 empty] | - |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- |  | - |  | 8 |  | 2 |  | 660LTS0041B | - | DEBUTANIZER | PRESSURE DP |  |  | W/T SEAL+CAPILLARY | - |  | L | ST1D | BPCS/SIS | CONV |  | 150 | 2650 |  | mm | 214359C-6602-PID-0021-0215 |  |  |  |  | 660-2-Fractionation | - |  | - | - | 3 | 660L0041 | N | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-430 / PART 1 FOLIO 2 | CI6 | NO | - | NI (NOT INSULATED) | - | - | -1736 | mmH2O 4°C | - | -708 | mmH2O 4°C | - | -10000 | mmH2O 4°C | - | 10000 | mmH2O 4°C | - | [6 empty] | INT | NR |  | - | - | [6 empty] | 660BJMS155/P4 |  | E10201 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Phase:Gas / Group:1 | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- |  | - |  | 11 |  | 2 |  | 660LTS0041BA | - | DEBUTANIZER | OUTPUT CONVERTER |  |  | - | - |  | ITR | ST1D | BPCS/SIS | S-PLC | [5 empty] | 214359C-6602-PID-0021-0215 |  |  |  |  | 660-2-Fractionation | - |  | - | - | 3 | 660L0041 | N | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [5 empty] | AI11 | INT | NR |  | - | - | [6 empty] | - |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- |  | - |  | 14 |  | 2 |  | 660LTS0041BB | - | DEBUTANIZER | OUTPUT CONVERTER |  |  | - | - |  | ITR | ST1C | BPCS/SIS | DCS | [5 empty] | 214359C-6602-PID-0021-0215 |  |  |  |  | 660-2-Fractionation | - |  | - | - | 3 | 660L0041 | N | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [5 empty] | AI11 | EXT | NR |  | - | - | [6 empty] | - |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- |  | - |  | 9 |  | 2 |  | 660LTS0041C | - | DEBUTANIZER | PRESSURE DP |  |  | W/T SEAL+CAPILLARY | - |  | L | ST1D | BPCS/SIS | CONV |  | 150 | 2650 |  | mm | 214359C-6602-PID-0021-0215 |  |  |  |  | 660-2-Fractionation | - |  | - | - | 3 | 660L0041 | N | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-430 / PART 1 FOLIO 2 | CI6 | NO | - | NI (NOT INSULATED) | - | - | -1736 | mmH2O 4°C | - | -708 | mmH2O 4°C | - | -10000 | mmH2O 4°C | - | 10000 | mmH2O 4°C | - | [6 empty] | INT | NR |  | - | - | [6 empty] | 660BJMS155/P10 |  | E10201 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Phase:Gas / Group:1 | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- |  | - |  | 12 |  | 2 |  | 660LTS0041CA | - | DEBUTANIZER | OUTPUT CONVERTER |  |  | - | - |  | ITR | ST1D | BPCS/SIS | S-PLC | [5 empty] | 214359C-6602-PID-0021-0215 |  |  |  |  | 660-2-Fractionation | - |  | - | - | 3 | 660L0041 | N | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [5 empty] | AI11 | INT | NR |  | - | - | [6 empty] | - |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- |  | - |  | 15 |  | 2 |  | 660LTS0041CB | - | DEBUTANIZER | OUTPUT CONVERTER |  |  | - | - |  | ITR | ST1C | BPCS/SIS | DCS | [5 empty] | 214359C-6602-PID-0021-0215 |  |  |  |  | 660-2-Fractionation | - |  | - | - | 3 | 660L0041 | N | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [5 empty] | AI11 | EXT | NR |  | - | - | [6 empty] | - |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV07 | - | 4 | - | 1 | - | 660UYS5056 | - | On-ff Valve 660UVS5056 | AIR SOLENOID SPRING | - | - | SOLENOID ONLY | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5056 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS500/C01-C02 | - | E10207 | 660IADM512/07 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5056-SP
- | - | UV12 | - | 3 | - | 1 | - | 660UYS5305A | - | On-ff Valve 660UVS5305 | AIR SOLENOID SPRING | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5305 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS500/C03-C04 | - | E10207 | 660IADM514/04 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5305A-SP
- | - | - | - | 2 | - | 1 | - | 660BS5301A | - | PILOT FLAME | FLAME SWITCH | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660B5301A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | EXT_230V | NR | - | - | - | - | - | - | - | - | - | 660BJMS505/P05 | - | E10202* | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660BS5301B | - | PILOT FLAME | FLAME SWITCH | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660B5301B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | EXT_230V | NR | - | - | - | - | - | - | - | - | - | 660BJMS505/P06 | - | E10202* | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- |  | UV05 | - | 3 |  | 2 |  | 660HLS5202 | - | Feed line to Debutanizer | TPL OPEN/CLOSE | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5202 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- |  | UV05 | - | 1 |  | 2 |  | 660UVS5202 | - | Feed line to Debutanizer | ON OFF VALVE | - | - | - | - | - | L | - | BPCS/SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5202 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA007 | CI9 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - |  | - | With solenoid | - | - | - | - | - | - | - | - | 660-3"-P-2219.0-1BB1 | - | - | - | - | - | - | - | - | - | - | Annex II Module H | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-UVS -5202-SP
- |  | UV05 | - | 2 |  | 2 |  | 660UYS5202 | - | Feed line to Debutanizer | AIR SOLENOID SPRING | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5202 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS114/C01-C02 |  | E10207 | 660IADM516/09 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-UVS -5202-SP
- |  | UV05 | - | 5 |  | 2 |  | 660UZSH5202 | - | Feed line to Debutanizer | LIMIT SWITCH | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5202 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS102/P10 |  | With UZSL | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-UVS -5202-SP
- |  | UV05 | - | 4 |  | 2 |  | 660UZSL5202 | - | Feed line to Debutanizer | LIMIT SWITCH | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5202 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS102/P09 |  | E10205 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-UVS -5202-SP
- |  | UV05 | - | 6 |  | 2 |  | 660XA5202 | - | Feed line to Debutanizer | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5202 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- |  | UV05 | - | 3 |  | 2 |  | 660HLS5203 | - | Feed line to Debutanizer | TPL OPEN/CLOSE | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5203 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- |  | UV05 | - | 1 |  | 2 |  | 660UVS5203 | - | Feed line to Debutanizer | ON OFF VALVE | - | - | - | - | - | L | - | BPCS/SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5203 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA007 | CI9 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - |  | - | With solenoid | - | - | - | - | - | - | - | - | 660-3"-P-2219.0-1BB1 | - | - | - | - | - | - | - | - | - | - | Annex II Module H | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-UVS -5203-SP
- |  | UV05 | - | 2 |  | 2 |  | 660UYS5203 | - | Feed line to Debutanizer | AIR SOLENOID SPRING | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5203 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS111/C15-C16 |  | E10207 | 660IADM516/10 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-UVS -5203-SP
- |  | UV05 | - | 5 |  | 2 |  | 660UZSH5203 | - | Feed line to Debutanizer | LIMIT SWITCH | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5203 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS102/P12 |  | With UZSL | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-UVS -5203-SP
- |  | UV05 | - | 4 |  | 2 |  | 660UZSL5203 | - | Feed line to Debutanizer | LIMIT SWITCH | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5203 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS102/P11 |  | E10205 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-UVS -5203-SP
- |  | UV05 | - | 6 |  | 2 |  | 660XA5203 | - | Feed line to Debutanizer | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5203 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660AA5001 | - | BIODIESEL TO TANK FARM 891P0 | ALARM | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660A5001 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJAN501/ P01 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660AI5001 | - | BIODIESEL TO TANK FARM 891P0 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | 0 | 120 | - | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660A5001 | U | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660BJAN502/ P01 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660AT5001 | - | FLASH POINT ANALYZER FOR BIODIESEL | ANALYSER 230VAC | - | - | FLASH POINT | - | - | AS | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | FLASH POINT | - | 3 | 660A5001 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-DW-1576-0008/Pag9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | EXT_220V | NR | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | LA35 | - | - | - | 660-4"-P-2007.0-3BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TAH5001 | - | BIODIESEL TO TANK FARM 891P0 | ALARM | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | - | - | Alarm High (366) | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660A5001 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM551/ P13 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660FAL5001A | - | BIODIESEL TO TANK FARM 891P0 | ALARM | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660A5001 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM551/ P02 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660FAL5001B | - | BIODIESEL TO TANK FARM 891P0 | ALARM | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660A5001 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM551/ P01 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 1 | - | 660AAL5001 | - | BIODIESEL TO TANK FARM 891P0 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660A5001 | U | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660AA5002 | - | BIODIESEL TO TANK FARM 891P0 | ALARM | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660A5002 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJAN501/ P02 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660AI5002 | - | BIODIESEL TO TANK FARM 891P0 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | -25 | 15 | - | °C | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660A5002 | U | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660BJAN502/ P02 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660AT5002 | - | CLOUD POINT ANALYZER FOR BIODIESEL | ANALYSER 230VAC | - | - | CLOUD POINT | - | - | AS | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | CLOUD POINT | - | 3 | 660A5002 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-DW-1576-0008/Pag9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | EXT_220V | NR | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | LA35 | - | - | - | 660-4"-P-2007.0-3BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660FAL5002 | - | BIODIESEL TO TANK FARM 891P0 | ALARM | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660A5002 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM551/ P10 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660AAH5002 | - | BIODIESEL TO TANK FARM 891P0 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660A5002 | U | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660AA5003 | - | BIODIESEL TO TANK FARM 891P0 | ALARM | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660A5003 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NI12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660AI5003A | 660-AI -5003 | BIODIESEL TO TANK FARM 891P0 | INDICATION | - | - | - | - | - | AS | SdC | BPCS | DCS | - | 0,8 | 0,9 | - | Kg/m3 | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660A5003 | NbO2 | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | - | - | - | - | - | - | - | - | - | - | - | 660BJAN502/ P03 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660AT5003 | 660AT5003 | DENSITY ANALYZER FOR BIODIESEL | DENSIMETER LIQUID | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | DENSITY | - | 3 | 660A5003 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-DW-1576-0008/Pag9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | EXT_220V | NR | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | LA35 | - | - | - | 660-4"-P-2007.0-3BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660AY5003B | - | BIODIESEL TO TANK FARM 891P0 | INDICATION | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660A5003 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660BJAN502/ P04 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660AI5003C | - | BIODIESEL TO TANK FARM 891P0 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | 0 | 100 | - | C | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660A5003 | U | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660BJAN502/ P05 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660AA5004 | - | JET CUT : STREAM 961P0 | ALARM | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660A5004 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJAN501/ P03 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660AI5004 | - | JET CUT : STREAM 961P0 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | 150 | 350 | - | c | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660A5004 | U | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660BJAN502/ P06 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660AT5004 | - | DIST. FINAL POINT D86 ANALYZER FOR JET | ANALYSER 230VAC | - | - | DISTILLATION | - | - | AS | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | ASTM | - | 3 | 660A5004 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-DW-1576-0008/Pag10 | - | - | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | EXT_220V | NR | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | LA35 | - | - | - | 660-4"-P-2021.0-3BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TAH5004 | - | JET CUT : STREAM 961P0 | ALARM | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660A5004 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM551/ P14 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660FAL5004A | - | JET CUT : STREAM 961P0 | ALARM | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660A5004 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM551/ P04 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660FAL5004B | - | JET CUT : STREAM 961P0 | ALARM | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660A5004 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM551/ P03 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660AA5005 | - | JET CUT : STREAM 961P0 | ALARM | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660A5005 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJAN501/ P04 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660AI5005 | - | JET CUT : STREAM 961P0 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | -75 | -35 | - | C | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660A5005 | U | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660BJAN502/ P07 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660AT5005 | - | FREEZING POINT ANALYZER FOR JET | ANALYSER 230VAC | - | - | FREEZE POINT | - | - | AS | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | FREEZING POINT | - | 3 | 660A5005 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-DW-1576-0008/Pag10 | - | - | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | EXT_220V | NR | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | LA35 | - | - | - | 660-4"-P-2021.0-3BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660FAL5005 | - | JET CUT : STREAM 961P0 | ALARM | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660A5005 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM551/ P09 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660AA5006 | - | JET CUT : STREAM 961P0 | ALARM | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660A5006 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJAN501/ P06 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660AI5006 | - | JET CUT : STREAM 961P0 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | 30 | 60 | - | C | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660A5006 | U | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660BJAN502/ P08 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660AT5006 | - | FLASH POINT ANALYZER FOR JET | ANALYSER 230VAC | - | - | FLASH POINT | - | - | AS | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | FLASH POINT | - | 3 | 660A5006 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-DW-1576-0008/Pag10 | - | - | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | EXT_220V | NR | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | LA35 | - | - | - | 660-4"-P-2021.0-3BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660FAL5006 | - | JET CUT : STREAM 961P0 | ALARM | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660A5006 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM551/ P11 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660AAL5006 | - | JET CUT : STREAM 961P0 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660A5006 | U | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660AA5007 | - | JET CUT : STREAM 961P0 | ALARM | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660A5007 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NI12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660AI5007A | 660-AI -5007 | JET CUT : STREAM 961P0 | INDICATION | - | - | - | - | - | AS | SdC | BPCS | DCS | - | 0,7 | 0,8 | - | Kg/m3 | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660A5007 | NbO2 | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | - | - | - | - | - | - | - | - | - | - | - | 660BJAN502/ P09 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660AT5007 | - | DENSITY ANALYZER FOR JET | DENSIMETER LIQUID | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | DENSITY | - | 3 | 660A5007 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-DW-1576-0008/Pag10 | - | - | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | EXT_220V | NR | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | LA35 | - | - | - | 660-4"-P-2021.0-3BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660AY5007B | - | DENSITY ANALYZER FOR JET | INDICATION | - | - | - | N | - | CRD | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | DENSITY | - | 3 | 660A5007 | U | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660BJAN502/ P10 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660AI5007C | - | JET CUT : STREAM 961P0 | INDICATION | - | - | - | - | - | AS | SdC | BPCS | DCS | - | 0 | 250 | - | °C | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660A5007 | NbO2 | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | - | - | - | - | - | - | - | - | - | - | - | 660BJAN502/ P11 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660AA5008 | - | NAPHTA CUT: STREAM 753P0 | ALARM | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660A5008 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJAN501/ P07 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660AI5008 | - | NAPHTA CUT: STREAM 753P0 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | 0 | 1400 | - | mBar | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660A5008 | U | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660BJAN502/ P12 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660AT5008 | - | VAPOR PRESSURE ANALYZER FOR NAPHTHA | ANALYSER 230VAC | - | - | VAPOR PRESSURE | - | - | AS | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | VP | - | 3 | 660A5008 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-DW-1576-0008/Pag11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | EXT_220V | NR | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | LA35 | - | - | - | 660-6"-P-2042.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660TAH5008 | - | NAPHTA CUT: STREAM 753P0 | ALARM | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660A5008 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM551/ P15 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660FAL5008A | - | NAPHTA CUT: STREAM 753P0 | ALARM | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660A5008 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM551/ P06 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 1 | - | 660FAL5008B | - | NAPHTA CUT: STREAM 753P0 | ALARM | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660A5008 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM551/ P05 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 1 | - | 660AAH5008 | - | NAPHTA CUT: STREAM 753P0 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0222 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660A5008 | U | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660AA5010 | - | Analyzer O2 660F5001 - 660AT5010 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | Low Alarm (1) | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660A5010 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660AI5010 | - | Analyzer O2 660F5001 - 660AT5010 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - |  | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660A5010 | N | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660AT5010 | - | Analyzer O2 660F5001 | O2 24VDC | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 25 | Low Alarm (1) | %volO2 | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | Alarm L: 1 | - | O2 | - | 3 | 660A5010 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | - | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | EXT_24V | NR | - | NR | - | - | - | - | - | - | - | 660BJM532/P01 | - | E10212 | - | - | - | - | - | LA35 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660AA5011B | - | Analyzer CH4 660F5001 - 660AT5011 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660A5011 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660AI5011A | - | Analyzer CO/CH4 660F5001 - 660AT5011 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660A5011 | N | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660AI5011B | - | Analyzer CO/CH4 660F5001 - 660AT5011 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660A5011 | N | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660AT5011A | 660-AT -5011 | 660-F-5001 - 660AT5011 CO | CO 24VDC | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 1000 | High Alarm (250) | ppmCO | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | Alarm H: 250 | - | - | - | 3 | 660A5011 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | - | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | EXT_24V | NR | - | NR | - | - | - | - | - | - | - | 660BJM532/P02 | - | E10218 | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660AT5011B | - | 660-F-5001 - 660AT5011 CH4 | CH4 24VDC | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 5 | High Alarm (1) | %volCH4 | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | Alarm H: 1 | - | - | - | 3 | 660A5011 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | - | - | - | - | - | - | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | - | NR | - | NR | - | - | - | - | - | - | - | 660BJM532/P03 | - | with AT | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660AA5011A | - | Analyzer CO 660F5001 - 660AT5011 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | High Alarm (100) | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660A5011 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660BE5301A | - | PILOT FLAME | FLAME DETECTOR | - | - | - | - | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660B5301A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI2 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | bar | Gage | 4 | bar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660BS5301C | - | PILOT FLAME | FLAME SWITCH | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660B5301C | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | EXT_230V | NR | - | - | - | - | - | - | - | - | - | 660BJMS505/P07 | - | E10202* | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660BSLL5301A | - | PILOT FLAME - 660BE5301A | FLAME DET. BURNER | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660B5301A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660BY5301A | - | PILOT FLAME - 660BE5301A | CDE TOR | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660B5301A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660BE5301B | - | PILOT FLAME | FLAME DETECTOR | - | - | - | - | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660B5301B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI2 | NO | - | CC | - | - | - | - | - | - | - | - | - | bar | Gage | 4 | bar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660BS5301D | - | PILOT FLAME | FLAME SWITCH | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660B5301D | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | EXT_230V | NR | - | - | - | - | - | - | - | - | - | 660BJMS505/P08 | - | E10202* | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660BSLL5301B | - | PILOT FLAME - 660BE5301B | FLAME DET. BURNER | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660B5301B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660BY5301B | - | PILOT FLAME - 660BE5301B | CDE TOR | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660B5301B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660BE5301C | - | PILOT FLAME | FLAME DETECTOR | - | - | - | - | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660B5301C | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI2 | NO | - | CC | - | - | - | - | - | - | - | - | - | bar | Gage | 4 | bar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- |  | - |  | 10 |  | 2 |  | 660LZSL5191A | - | FROM 660 D 5002 (DIESEL MODE) | LIMIT SWITCH |  |  | - | - |  | L | ST1D | BPCS/SIS | S-PLC | [5 empty] | 214359C-6602-PID-0021-0213 |  |  |  |  | 660-2-Fractionation | - |  | - | - | 7 | 660L5191 | N | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [5 empty] | DI10 | INT |  |  | - | - | [6 empty] | 660BJMS505/PR09 |  | E10204 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660BSLL5301C | - | PILOT FLAME - 660BE5301C | FLAME DET. BURNER | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660B5301C | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660BY5301C | - | PILOT FLAME - 660BE5301C | CDE TOR | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660B5301C | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660BE5301D | - | PILOT FLAME | FLAME DETECTOR | - | - | - | - | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660B5301D | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI2 | NO | - | CC | - | - | - | - | - | - | - | - | - | bar | Gage | 4 | bar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- |  | - |  | 11 |  | 2 |  | 660LZSL5191B | - | 660 D 5002 (JET MODE) | LIMIT SWITCH |  |  | - | - |  | L | ST1D | BPCS/SIS | S-PLC | [5 empty] | 214359C-6602-PID-0021-0213 |  |  |  |  | 660-2-Fractionation | - |  | - | - | 7 | 660L5191 | N | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [5 empty] | DI10 | INT |  |  | - | - | [6 empty] | 660BJMS505/PR10 |  | E10204 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660BSLL5301D | - | PILOT FLAME - 660BE5301D | FLAME DET. BURNER | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660B5301D | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660BY5301D | - | PILOT FLAME - 660BE5301D | CDE TOR | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660B5301D | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660BSLL5370 | - | BURNER FLAME DETECTION ELEMENT - 660BE5370 | FLAME DET. BURNER | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660B5370 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660BS5370 | - | BURNER FLAME DETECTION ELEMENT - 660BE5370 | FLAME SWITCH | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660B5370 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660BSLL5372 | - | BURNER FLAME DETECTION ELEMENT - 660BE5372 | FLAME DET. BURNER | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660B5372 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660BS5372 | - | BURNER FLAME DETECTION ELEMENT - 660BE5372 | FLAME SWITCH | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660B5372 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660BSLL5374 | - | BURNER FLAME DETECTION ELEMENT - 660BE5374 | FLAME DET. BURNER | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660B5374 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660BS5374 | - | BURNER FLAME DETECTION ELEMENT - 660BE5374 | FLAME SWITCH | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660B5374 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660BSLL5376 | - | BURNER FLAME DETECTION ELEMENT - 660BE5376 | FLAME DET. BURNER | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660B5376 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660BS5376 | - | BURNER FLAME DETECTION ELEMENT - 660BE5376 | FLAME SWITCH | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660B5376 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 1 | - | 1 | - | 660HSE0004AAA | - | 660-E-0004AB LOCAL ESD | ESD PB | - | - | NORMALLY CLOSE | - | - | L | - | BPCS/SIS | VSD | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660EM0004AA | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 3 | - | 1 | - | 660HLSE0004AA | - | 660-E-0004AB START/STOP | TPL START / STOP | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM0004AA | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 4 | - | 1 | - | 660HLSE0004AAM | - | 660-E-0004AB LOCAL ESD | CDE TOR | - | - | NORMALLY OPEN | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM0004AA | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 5 | - | 1 | - | 660HLSE0004AAA | - | 660-E-0004AB TRIP | CDE TOR | - | - | NORMALLY CLOSE | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM0004AA | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 6 | - | 1 | - | 660HLSE0004AAR | - | 660-E-0004AB RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM0004AA | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 7 | - | 1 | - | 660XSE0004AA | - | 660-E-0004AB ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1D | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660EM0004AA | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 8 | - | 1 | - | 660XAE0004AA | - | 660-E-0004AB ELEC FAULT | ALARM | - | - | - | - | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660EM0004AA | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 9 | - | 1 | - | 660XSE0004AAF | - | 660-E-0004AB VSD FAULT | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660EM0004AA | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 10 | - | 1 | - | 660XAE0004AAF | - | 660-E-0004AB VSD FAULT | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660EM0004AA | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 11 | - | 1 | - | 660XAE0004AAD | - | 660-E-0004AB DISC SECU | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660EM0004AA | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 12 | - | 1 | - | 660SIE0004AA | - | 660-E-0004AB SPEED | SPEED | - | - | - | - | - | ESS | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660EM0004AA | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 13 | - | 1 | - | 660SCE0004AA | - | 660-E-0004AB SPEED SET POINT | OPER SETPOINT | - | - | - | - | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660EM0004AA | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO12 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV15 | - | 9 | - | 1 | - | 660HS5001A | - | 660-UVS-5001 CLOSE | ESD PB | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS502/P01 | - | E10204 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 3 | - | 1 | - | 660HLSE0004AB | - | 660-E-0004BB START/STOP | TPL START / STOP | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM0004AB | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 4 | - | 1 | - | 660HLSE0004ABM | - | 660-E-0004BB LOCAL ESD | CDE TOR | - | - | NORMALLY OPEN | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM0004AB | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 5 | - | 1 | - | 660HLSE0004ABA | - | 660-E-0004BB TRIP | CDE TOR | - | - | NORMALLY CLOSE | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM0004AB | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 6 | - | 1 | - | 660HLSE0004ABR | - | 660-E-0004BB RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM0004AB | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 7 | - | 1 | - | 660XSE0004AB | - | 660-E-0004BB ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660EM0004AB | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 8 | - | 1 | - | 660XAE0004AB | - | 660-E-0004BB ELEC FAULT | ALARM | - | - | - | - | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660EM0004AB | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 9 | - | 1 | - | 660XAE0004ABD | - | 660-E-0004BB DISC SECU | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660EM0004AB | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 1 | - | 1 | - | 660HSE0006A | 660-HSE -0006AA | 660-E-0006A LOCAL ESD | ESD PB | - | - | NORMALLY CLOSE | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660EM0006A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJMS155/P11 | - | E10204 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 2 | - | 1 | - | 660HSE0006AB | - | 660-E-0006A LOCAL ESD B | ESD PB | - | - | NORMALLY CLOSE | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660EM0006A | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 3 | - | 1 | - | 660HLSE0006A | - | 660-E-0006A START/STOP | TPL START / STOP | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM0006A | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 4 | - | 1 | - | 660HLSE0006AM | - | 660-E-0006A LOCAL ESD | CDE TOR | - | - | NORMALLY OPEN | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM0006A | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 5 | - | 1 | - | 660HLSE0006AA | - | 660-E-0006A TRIP | CDE TOR | - | - | NORMALLY CLOSE | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM0006A | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 6 | - | 1 | - | 660HLSE0006AR | - | 660-E-0006A RUNNING STATUS | CONTACT | - | - | NORMALLY CLOSE | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM0006A | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 7 | - | 1 | - | 660XSE0006A | - | 660-E-0006A ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660EM0006A | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 8 | - | 1 | - | 660XAE0006A | - | 660-E-0006A ELEC FAULT | ALARM | - | - | - | - | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660EM0006A | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 9 | - | 1 | - | 660XAE0006AD | - | 660-E-0006A DISC SECU | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660EM0006A | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 1 | - | 1 | - | 660HSE0006B | 660-HSE -0006BA | 660-E-0006B LOCAL ESD | ESD PB | - | - | NORMALLY CLOSE | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660EM0006B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJMS155/P12 | - | E10204 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 2 | - | 1 | - | 660HSE0006BB | - | 660-E-0006B LOCAL ESD B | ESD PB | - | - | NORMALLY CLOSE | - | - | L | - | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660EM0006B | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 3 | - | 1 | - | 660HLSE0006B | - | 660-E-0006B START/STOP | TPL START / STOP | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM0006B | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 4 | - | 1 | - | 660HLSE0006BM | - | 660-E-0006B LOCAL ESD | CDE TOR | - | - | NORMALLY OPEN | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM0006B | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 5 | - | 1 | - | 660HLSE0006BA | - | 660-E-0006B TRIP | CDE TOR | - | - | NORMALLY CLOSE | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM0006B | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 6 | - | 1 | - | 660HLSE0006BR | - | 660-E-0006B RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM0006B | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 7 | - | 1 | - | 660XSE0006B | - | 660-E-0006B ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660EM0006B | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 8 | - | 1 | - | 660XAE0006B | - | 660-E-0006B ELEC FAULT | ALARM | - | - | - | - | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660EM0006B | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 9 | - | 1 | - | 660XAE0006BD | - | 660-E-0006B DISC SECU | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660EM0006B | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 1 | - | 1 | - | 660HSE5102AA | - | 660-EM-5002A LOCAL ESD A | ESD PB | - | - | NORMALLY CLOSE | - | - | L | ST1 | BPCS/SIS | VSD | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5002A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 3 | - | 1 | - | 660HLSE5102A | - | 660-EM-5002A START / STOP | TPL START / STOP | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660EM5002A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 4 | - | 1 | - | 660HLSE5102AM | - | 660-EM-5002A START | CDE TOR | - | - | - | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5002A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 5 | - | 1 | - | 660HLSE5102AA | - | 660-EM-5002A TRIP | CDE TOR | - | - | NORMALLY CLOSE | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5002A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 6 | - | 1 | - | 660HLSE5102AR | - | 660-EM-5002A RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5002A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 7 | - | 1 | - | 660XSE5102A | - | 660-EM-5002A ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5002A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 8 | - | 1 | - | 660XAE5102A | - | 660-EM-5002A ELEC FAULT | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660EM5002A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 9 | - | 1 | - | 660XSE5102AF | - | 660-EM-5002B VSD FAULT | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5002A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 10 | - | 1 | - | 660XAE5102AF | - | 660-EM-5002B VSD FAULT | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660EM5002A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 11 | - | 1 | - | 660XAE5102AD | - | 660-EM-5002A DISC SECU | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660EM5002A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 12 | - | 1 | - | 660SIE5102A | - | 660-EM-5002B SPEED | SPEED | - | - | - | N | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660EM5002A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 13 | - | 1 | - | 660SCE5102A | - | 660-EM-5002B SPEED SET POINT | OPER SETPOINT | - | - | - | N | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660EM5002A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO12 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 14 | - | 1 | - | 660HC5102A | - | 660-EM-5002B SPEED SP | INDICATION | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660EM5002A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 7 | - | 1 | - | 660HS5013 | 660-HS -5013A | 660-UV-5013 | PB SOFT | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5013 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS500/P01 | - | E10204 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 16 | - | 1 | - | 660HSE5102A | - | 660-EM-5002A LOCAL ESD | ESD PB | - | - | NORMALLY CLOSE | - | - | L | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5002A | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 1 | - | 1 | - | 660HSE5102BA | - | 660-EM-5002B LOCAL ESD A | ESD PB | - | - | NORMALLY CLOSE | - | - | L | - | BPCS/SIS | VSD | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5002B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 3 | - | 1 | - | 660HLSE5102B | - | 660-EM-5002B START / STOP | TPL START / STOP | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660EM5002B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 4 | - | 1 | - | 660HLSE5102BM | - | 660-EM-5002B START | CDE TOR | - | - | - | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5002B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 5 | - | 1 | - | 660HLSE5102BA | - | 660-EM-5002B TRIP | CDE TOR | - | - | NORMALLY CLOSE | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5002B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 6 | - | 1 | - | 660HLSE5102BR | - | 660-EM-5002B RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5002B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 7 | - | 1 | - | 660XSE5102B | - | 660-EM-5002B ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5002B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 8 | - | 1 | - | 660XAE5102B | - | 660-EM-5002B ELEC FAULT | ALARM | - | - | - | N | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660EM5002B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 9 | - | 1 | - | 660XSE5102BF | - | 660-EM-5002B VSD FAULT | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5002B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 10 | - | 1 | - | 660XAE5102BF | - | 660-EM-5002B VSD FAULT | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660EM5002B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 11 | - | 1 | - | 660XAE5102BD | - | 660-EM-5002B DISC SECU | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660EM5002B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 12 | - | 1 | - | 660SIE5102B | - | 660-EM-5002B SPEED | SPEED | - | - | - | N | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660EM5002B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 13 | - | 1 | - | 660SCE5102B | - | 660-EM-5002B SPEED SET POINT | OPER SETPOINT | - | - | - | N | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660EM5002B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO12 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 14 | - | 1 | - | 660HC5102B | - | 660-EM-5002B SPEED SP | INDICATION | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660EM5002B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 4 | - | 1 | - | 660UZSH5013 | - | 660-UV-5013 OPEN | LIMIT SWITCH | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5013 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS500/P03 | - | With UZSL | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 16 | - | 1 | - | 660HSE5102B | - | 660-EM-5002B LOCAL ESD | ESD PB | - | - | - | - | - | CRD | - | BPCS/SIS | VSD | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5002B | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 1 | - | 1 | - | 660HSE5006AA | 660-HS -5006AA | 660-EM-5006A LOCAL ESD A | ESD PB | - | - | NORMALLY CLOSE | - | - | L | - | BPCS/SIS | VSD | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5006A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 2 | - | 1 | - | 660HS5006AB | - | 660-EM-5006A LOCAL ESD B | ESD PB | - | - | NORMALLY CLOSE | - | - | L | ST1D | BPCS/SIS | VSD | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5006A | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 3 | - | 1 | - | 660HLSE5006A | - | 660-EM-5006A START / STOP | TPL START / STOP | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5006A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 4 | - | 1 | - | 660HLSE5006AM | - | 660-EM-5006A START | CDE TOR | - | - | NORMALLY OPEN | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5006A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 5 | - | 1 | - | 660HLSE5006AA | - | 660-EM-5006A TRIP | CDE TOR | - | - | NORMALLY CLOSE | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5006A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 6 | - | 1 | - | 660HLSE5006AR | - | 660-EM-5006A RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5006A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 7 | - | 1 | - | 660XSE5006A | - | 660-EM-5006A ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5006A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 8 | - | 1 | - | 660XAE5006A | - | 660-EM-5006A ELEC FAULT | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660EM5006A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 9 | - | 1 | - | 660XSE5006AF | - | 660-EM-5006A VSD FAULT | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5006A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 10 | - | 1 | - | 660XAE5006AF | - | 660-EM-5006A VSD FAULT | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660EM5006A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 11 | - | 1 | - | 660XAE5006AD | - | 660-EM-5006A DISC SECU | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660EM5006A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 12 | - | 1 | - | 660SIE5006A | - | 660-EM-5006A SPEED | SPEED | - | - | - | N | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660EM5006A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 13 | - | 1 | - | 660SCE5006A | 660-SC -E5006A | 660-EM-5006A SPEED SET POINT | OPER SETPOINT | - | - | - | N | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660EM5006A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO12 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 14 | - | 1 | - | 660HC5006A | - | 660-EM-5006A SPEED SP | INDICATION | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660EM5006A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV07 | - | 5 | - | 1 | - | 660UZSH5056 | - | 660-UVS-5056 OPEN | LIMIT SWITCH | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5056 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS500/P04 | - | With UZSL | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV15 | - | 9 | - | 1 | - | 660HS5002A | - | 660-UVS-5002 CLOSE | ESD PB | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5002 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS502/P03 | - | E10204 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 1 | - | 1 | - | 660HSE5006BA | - | 660-EM-5006B LOCAL ESD A | ESD PB | - | - | NORMALLY CLOSE | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5006B | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 2 | - | 1 | - | 660HS5006BB | - | 660-EM-5006B LOCAL ESD B | ESD PB | - | - | NORMALLY CLOSE | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5006B | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 3 | - | 1 | - | 660HLSE5006B | - | 660-EM-5006B START / STOP | TPL START / STOP | - | - | NORMALLY CLOSE | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660EM5006B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 4 | - | 1 | - | 660HLSE5006BM | - | 660-EM-5006B START | CDE TOR | - | - | - | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5006B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 5 | - | 1 | - | 660HLSE5006BA | - | 660-EM-5006B TRIP | CDE TOR | - | - | NORMALLY CLOSE | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5006B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 6 | - | 1 | - | 660HLSE5006BR | - | 660-EM-5006B RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5006B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 7 | - | 1 | - | 660XSE5006B | - | 660-EM-5006B ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5006B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 8 | - | 1 | - | 660XAE5006B | - | 660-EM-5006B ELEC FAULT | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660EM5006B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 9 | - | 1 | - | 660XAE5006BD | - | 660-EM-5006B DISC SECU | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660EM5006B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 3 | - | 1 | - | 660UZSH5150 | - | PROCCES FLUID TO FT 5154/5155 | LIMIT SWITCH | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5150 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS500/P05 | - | With UZSL | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 7 | - | 1 | - | 660HS5014 | 660-HS -5014A | 660-UVS-5014 | ESD PB | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5014 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS502/P05 | - | E10204 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 1 | - | 1 | - | 660HSE5006CA | - | 660-EM-5006C LOCAL ESD A | ESD PB | - | - | NORMALLY CLOSE | - | - | L | - | BPCS/SIS | VSD | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5006C | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 2 | - | 1 | - | 660HS5006CB | - | 660-EM-5006C LOCAL ESD B | ESD PB | - | - | NORMALLY CLOSE | - | - | L | ST1D | BPCS/SIS | VSD | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5006C | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 3 | - | 1 | - | 660HLSE5006C | - | 660-EM-5006C START / STOP | TPL START / STOP | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5006C | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 4 | - | 1 | - | 660HLSE5006CM | - | 660-EM-5006C START | CDE TOR | - | - | NORMALLY OPEN | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5006C | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 5 | - | 1 | - | 660HLSE5006CA | - | 660-EM-5006C TRIP | CDE TOR | - | - | NORMALLY CLOSE | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5006C | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 6 | - | 1 | - | 660HLSE5006CR | - | 660-EM-5006C RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5006C | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 7 | - | 1 | - | 660XSE5006C | - | 660-EM-5006C ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5006C | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 8 | - | 1 | - | 660XAE5006C | - | 660-EM-5006C VSD FAULT | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660EM5006C | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 9 | - | 1 | - | 660XSE5006CF | - | 660-EM-5006C ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5006C | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 10 | - | 1 | - | 660XAE5006CF | - | 660-EM-5006C VSD FAULT | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660EM5006C | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 11 | - | 1 | - | 660XAE5006CD | - | 660-EM-5006C DISC SECU | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660EM5006C | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 12 | - | 1 | - | 660SIE5006C | - | 660-EM-5006C SPEED | SPEED | - | - | - | N | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660EM5006C | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 13 | - | 1 | - | 660SCE5006C | - | 660-EM-5006C SPEED SET POINT | OPER SETPOINT | - | - | - | N | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660EM5006C | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO12 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 14 | - | 1 | - | 660HC5006C | - | 660-EM-5006C SPEED SP | INDICATION | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660EM5006C | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV07 | - | 3 | - | 1 | - | 660UZSH5291 | - | DIESEL MODE FROM 660 E 5008 | LIMIT SWITCH | - | - | - | N | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5291 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS500/P06 | - | With UZSL | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV15 | - | 5 | - | 1 | - | 660UZSH5001 | - | 660-UVS-5001 OPEN | LIMIT SWITCH | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | Alarm L: Closed | - | - | - | 7 | 660U5001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS502/P07 | - | With UZSL | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 1 | - | 1 | - | 660HSE5006DA | - | 660-EM-5006D LOCAL ESD A | ESD PB | - | - | NORMALLY CLOSE | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5006D | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 3 | - | 1 | - | 660HLSE5006D | - | 660-EM-5006D START / STOP | TPL START / STOP | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660EM5006D | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 4 | - | 1 | - | 660HLSE5006DM | - | 660-EM-5006D START | CDE TOR | - | - | - | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5006D | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 5 | - | 1 | - | 660HLSE5006DA | - | 660-EM-5006D TRIP | CDE TOR | - | - | NORMALLY CLOSE | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5006D | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 6 | - | 1 | - | 660HLSE5006DR | - | 660-EM-5006D RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5006D | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 7 | - | 1 | - | 660XSE5006D | - | 660-EM-5006D ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5006D | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 8 | - | 1 | - | 660XAE5006D | - | 660-EM-5006D ELEC FAULT | ALARM | - | - | - | N | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660EM5006D | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 9 | - | 1 | - | 660XAE5006DD | - | 660-EM-5006D DISC SECU | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660EM5006D | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 5 | - | 1 | - | 660UZSL5013 | - | 660-UV-5013 CLOSE | LIMIT SWITCH | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5013 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS500/P07 | - | E10205 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV15 | - | 5 | - | 1 | - | 660UZSH5002 | - | 660-UVS-5002 OPEN | LIMIT SWITCH | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | Alarm L: Closed | - | - | - | 7 | 660U5002 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS502/P08 | - | With UZSL | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 12 | - | 1 | - | 660SI5006D | - | 660-EM-5006D SPEED | SPEED | - | - | - | - | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660EM5006D | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 13 | - | 1 | - | 660XA5006DF | - | 660-EM-5006D VSD FAULT | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660EM5006D | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 14 | - | 1 | - | 660SC5006D | - | 660-EM-5006D SPEED SET POINT | OPER SETPOINT | - | - | - | - | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660EM5006D | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 15 | - | 1 | - | 660XS5006DF | - | 660-EM-5006D VSD FAULT | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5006D | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660FE0006 | - | NAPHTHA TO BATTERY LIMIT | ORIFICE | - | - | - | - | - | L | - | BPCS/SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660F0006 | R1D2 | SAME_POSITION | - | - | - | - | TIP-660-5501-I | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | CC | - | - | 0 | mbar | - | 100 | mbar | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-26.1-B1A | OTHER | L | 8 | 11.5 | 40 | 122 | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-FE -0006-SP
- | - | - | - | 2 | - | 1 | - | 660FT0006 | - | FT0006 G.O DESULFURE -> STOCK | PRESSURE DP | - | - | TRANSM ALIM EXT | - | - | L | ST7 | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F0006 | M | SAME_POSITION | - | - | - | - | TIP-660-5501-I | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | EXT | NR | - | - | - | - | - | - | - | - | - | 66BR1M, 09-10 | - | - | - | - | - | - | - | JB info by OSBL | - | - | - | 660-6"-P-26.1-B1A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660FTS0006B | - | FTS0006B SECU G.O DESULFURE -> STOCK | PRESSURE DP | - | - | TRANSM ALIM EXT | - | - | L | ST1D | BPCS/SIS | S-PLC | - | 0 | 16 | - | m3/h | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F0006 | M | SAME_POSITION | - | - | - | - | TIP-660-5501-I | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | EXT | NR | - | - | - | - | - | - | - | - | - | 600BE12, 21-22 | - | - | - | - | - | - | - | JB info by OSBL | - | - | - | 660-6"-P-26.1-B1A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660FI0006 | - | FROM 660E0004A - 660FT0006 | FLOW INDICATOR | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660F0006 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660FSL0006B | - | FROM 660E0004A - 660FTS0006B | SOFT THERSHOLD | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | TBD BY TTE(Job Card) | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660F0006 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660FC0007 | - | TO 660C0001 - 660FT0007 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660F0007 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660FE0007 | - | PUMP DISCHARGE TO FRACTIONATOR | ORIFICE | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660F0007 | R1D2 | SAME_POSITION | - | - | - | - | TIP-660-5506-I | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | - | - | 0 | mbar | - | 100 | mbar | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-2"-P-17.4-C3F | HC | L | 19.5 | 23 | 40 | 120 | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-FE -0007-SP
- | - | - | - | 3 | - | 1 | - | 660FT0007 | - | FT0007 ESSENCE TETE STRIPPER C0001 | PRESSURE DP | - | - | TRANSM ALIM EXT | - | - | L | ST7 | BPCS | DCS | - | 0 | 1.4 | - | m3/h | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F0007 | M | SAME_POSITION | - | - | - | - | TIP-660-5506-I | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 66BR1M, 11-12 | - | - | - | - | - | - | - | JB info by OSBL | - | - | - | 660-2"-P-17.4-C3F | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | CV01 | - | 4 | - | 1 | - | 660FV0007 | 660LV0008 | DEBUTANIZER OVERHEAD TO FRACTIONATOR | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660F0007 | R1D2 | SAME_POSITION | - | - | - | - | TIP-660-5507-I | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA004 | Cl9 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | 66BR1M/ 25,26 | - | - | - | - | - | - | - | - | - | - | - | 660-1"-P-17.5-3BB3 | OTHER | L | 19.43 | 23 | 40 | 120 | - | - | - | - | III module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FV -0007-SP
- | - | - | - | 1 | - | 1 | - | 660FC0017 | - | TO 660E5008 - 660FT0017 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660F0017 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660FE0017 | - | REFLUX TO DEBUTANIZER | ORIFICE | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660F0017 | R1D2 | SAME_POSITION | - | - | - | - | TIP-660-5502-I | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | - | - | 0 | mbar | - | 250 | mbar | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-2"-P-17.1-C3F | HC | L | 19.4 | 23 | 40 | 120 | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-FE -0017-SP
- | - | - | - | 3 | - | 1 | - | 660FT0017 | - | FT0017 REFLUX C0001 | PRESSURE DP | - | - | TRANSM ALIM EXT | - | - | L | ST1C | BPCS | DCS | - | 0 | 1.4 | - | m3/h | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F0017 | M | SAME_POSITION | - | - | - | - | TIP-660-5502-I | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | - | - | - | - | - | - | - | JB TBC by TTE | - | - | - | - | - | - | - | - | - | - | - | 660-2"-P-17.4-C3F | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | CV01 | - | 4 | - | 1 | - | 660FV0017 | 660TV0017 | REFLUX TO 660 C 0001 | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660F0017 | R1D2 | SAME_POSITION | - | - | - | - | TIP-660-5503-I | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA004 | Cl9 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | 66BR1M/ 19,20 | - | - | - | - | - | - | - | - | - | - | - | 660-2"-P-17.1-3BB3 | OTHER | L | 19.28 | 23 | 40 | 120 | - | - | - | - | III module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FV -0017-SP
- | - | - | - | 1 | - | 1 | - | 660FI5050 | - | FROM 660E5001 - 660FT5050 | FLOW INDICATOR | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0201 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660F5050 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660FE5050 | - | DIESEL TO CRACKING CHARGE PUMPS | ORIFICE | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0201 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660F5050 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | CC | - | - | 0 | mbar | - | 250 | mbar | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-4"-P-2001.0-3BB3 | OTHER | L | 5.45 | 19 | 260 | 343 | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-FE -5050-SP
- | - | - | - | 3 | - | 1 | - | 660FT5050 | - | FROM 660 E 5001 | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 45 | - | m³/h | 214359C-6602-PID-0021-0201 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5050 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-420 / PART 2 FOLIO 4 | CΙ2 | P | LP | TV2 | STD RC INS 220 / FOLIO 30 | - | 0 | mbar | - | 250 | mbar | - | -1000 | mbar | - | 1000 | mbar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM530/P01 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-4"-P-2001.0-3BB3 | OTHER | L | 5.45 | 19 | 260 | 343 | - | - | - | - | PED Fluid Group: 1. Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FT -5050-SP
- | - | - | - | 4 | - | 1 | - | 660FAL5050 | - | FROM 660E5001 - 660FT5050 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0201 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660F5050 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660FC5051 | - | BIOJET TO TANK FARM - 660FT5051 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0209 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660F5051 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660FT5051 | - | SBC TO TANK FARM | VORTEX | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 60 | - | m³/h | 214359C-6602-PID-0021-0209 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5051 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | GS RC INS 200 / Appendix 12-T13B | CI2 | NO | - | CC | - | - | 0 | m³/h | - | 60 | m³/h | - | 5.43 | m³/h | - | 143 | m³/h | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM530/P02 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-4"-P-2021.0-3BB1 | OTHER | L | 4.89 | 19 | 173 | 250 | - | - | - | - | I | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-FT -5051-SP
- | - | - | - | 3 | - | 1 | - | 660FT5055 | - | FROM 660 E 5001 | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 55 | - | m³/h | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5055 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-420 / PART 2 FOLIO 4 | CΙ2 | P | LP | TV3 | STD RC INS 220 / FOLIO 30 | - | 0 | mbar | - | 250 | mbar | - | -1000 | mbar | - | 1000 | mbar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM530/P03 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-4"-P-2007.0-3BB1 | OTHER | L | 5.18 | 19 | 40 | 260 | - | - | - | - | PED Fluid Group: 1. Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FT -5055-SP
- | - | - | - | 3 | - | 1 | - | 660FT5052 | - | FROM 660 G 5001A/B | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5052 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CC | - | - | 0 | mbar | - | 250 | mbar | - | - | mbar | - | - | - | - | - | - | - | - | - | - | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-8"-P-2009.1-3BB3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660FE5053 | - | INLET PASS TO REBOILER 660 F 5001 | ORIFICE | - | - | - | - | - | L | - | BPCS/SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660F5053 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | CC | - | - | 0 | mbar | - | 250 | mbar | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-8"-P-2009.1-3BB3 | OTHER | L | 8.77 | 19 | 357 | 390 | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-FE -5053-SP
- | - | - | - | 1 | - | 1 | - | 660LTS5193A | - | PRODUCT FRACTIONATOR RECEIVER | PRESSURE DP | - | - | W/T SEAL+CAPILLARY | - | - | L | ST1D | BPCS/SIS | CONV | - | 0 | 100 | - | % | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660L5193 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-430 / PART 1 FOLIO 2 | CI6 | NO | - | NI (NOT INSULATED) | - | - | -1658.5 | mmH2O 4°C | - | -647.36 | mmH2O 4°C | - | -10000 | mmH2O 4°C | - | 10000 | mmH2O 4°C | - | - | - | - | - | - | - | INT | NR | - | 660-LY-5193A | - | - | - | - | - | - | - | 660BJMS533/P01 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | OTHER | OTHER | 0.66 | 4 | 40 | 120 | - | - | - | - | PED Group: 1 Phase Gas | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-LTS -5193A-SP
- | - | - | - | 2 | - | 1 | - | 660LTS5193B | - | PRODUCT FRACTIONATOR RECEIVER | PRESSURE DP | - | - | W/T SEAL+CAPILLARY | - | - | L | ST1D | BPCS/SIS | CONV | - | 0 | 100 | - | % | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660L5193 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-430 / PART 1 FOLIO 2 | CI6 | NO | - | NI (NOT INSULATED) | - | - | -1658.5 | mmH2O 4°C | - | -647.36 | mmH2O 4°C | - | -10000 | mmH2O 4°C | - | 10000 | mmH2O 4°C | - | - | - | - | - | - | - | INT | NR | - | 660-LY-5193B | - | - | - | - | - | - | - | 660BJMS533/P02 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | OTHER | OTHER | 0.66 | 4 | 40 | 120 | - | - | - | - | PED Group: 1 Phase Gas | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-LTS -5193B-SP
- | - | - | - | 3 | - | 1 | - | 660LTS5193C | - | PRODUCT FRACTIONATOR RECEIVER | PRESSURE DP | - | - | W/T SEAL+CAPILLARY | - | - | L | ST1D | BPCS/SIS | CONV | - | 0 | 100 | - | % | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660L5193 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-430 / PART 1 FOLIO 2 | CI6 | NO | - | NI (NOT INSULATED) | - | - | -1658.5 | mmH2O 4°C | - | -647.36 | mmH2O 4°C | - | -10000 | mmH2O 4°C | - | 10000 | mmH2O 4°C | - | - | - | - | - | - | - | INT | NR | - | 660-LY-5193C | - | - | - | - | - | - | - | 660BJMS539/P01 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | OTHER | OTHER | 0.66 | 4 | 40 | 120 | - | - | - | - | PED Group: 1 Phase Gas | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-LTS -5193C-SP
- | - | - | - | 5 | - | 1 | - | 660FTS5053AA | - | FROM 660G5001AB - 660FTS5053ABC | OUTPUT CONVERTER | - | - | - | N | - | ITR | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5053 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660FTS5053BA | - | FROM 660G5001AB - 660FTS5053ABC | OUTPUT CONVERTER | - | - | - | N | - | ITR | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5053 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 1 | - | 660FTS5053CA | - | FROM 660G5001AB - 660FTS5053ABC | OUTPUT CONVERTER | - | - | - | N | - | ITR | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5053 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 1 | - | 660FTS5053AB | - | PROCESS FLUID FR 660F5001 - 660FTS5053ABC | OUTPUT CONVERTER | - | - | - | N | - | ITR | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5053 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | EXT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 9 | - | 1 | - | 660FTS5053BB | - | PROCESS FLUID FR 660F5001 - 660FTS5053ABC | OUTPUT CONVERTER | - | - | - | N | - | ITR | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5053 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | EXT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 10 | - | 1 | - | 660FTS5053CB | - | PROCESS FLUID FR 660F5001 - 660FTS5053ABC | OUTPUT CONVERTER | - | - | - | N | - | ITR | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5053 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | EXT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 11 | - | 1 | - | 660FI5053A | - | FROM 660G5001AB - 660FTS5053ABC | INDICATION | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660F5053 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 12 | - | 1 | - | 660FI5053B | - | FROM 660G5001AB - 660FTS5053ABC | INDICATION | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660F5053 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 13 | - | 1 | - | 660FI5053C | - | FROM 660G5001AB - 660FTS5053ABC | INDICATION | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660F5053 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 14 | - | 1 | - | 660FSLL5053AA | - | FROM 660G5001AB - 660FTS5053ABC | SOFT THERSHOLD | - | - | - | N | - | ITR | ST1D | BPCS/SIS | S-PLC | - | - | - | Low Alarm (91) / Low-Low alarm (91) | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660F5053 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 15 | - | 1 | - | 660FSLL5053BA | - | FROM 660G5001AB - 660FTS5053ABC | SOFT THERSHOLD | - | - | - | N | - | ITR | ST1D | BPCS/SIS | S-PLC | - | - | - | Low-Low alarm (91) | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660F5053 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 16 | - | 1 | - | 660FSLL5053CA | - | FROM 660G5001AB - 660FTS5053ABC | SOFT THERSHOLD | - | - | - | N | - | ITR | ST1D | BPCS/SIS | S-PLC | - | - | - | low low alarm (91) | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660F5053 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 17 | - | 1 | - | 660FALL5053 | - | FROM 660G5001AB - 660FTS5053ABC | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | low low Alarm (128) | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660F5053 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 18 | - | 1 | - | 660FAX5053 | - | FROM 660G5001AB - 660FTS5053ABC | SOFT CALCULATION | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660F5053 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 19 | - | 1 | - | 660FSL5053 | - | FROM 660G5001AB - 660FTS5053ABC | SOFT THERSHOLD | - | - | - | N | - | ITR | ST1C | BPCS/SIS | DCS | - | - | - | 130 | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660F5053 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 20 | - | 1 | - | 660FAL5053 | - | FROM 660G5001AB - 660FTS5053ABC | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | Law Alarm (135) | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660F5053 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 21 | - | 1 | - | 660FC5053 | - | FROM 660G5001AB - 660FTS5053ABC | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660F5053 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660FT5054 | - | FROM 660 E 5001 | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 7 | - | m³/h | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5054 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-420 / PART 2 FOLIO 4 | CΙ2 | P | LP | TV3 | STD RC INS 220 / FOLIO 30 | - | 0 | mbar | - | 125 | mbar | - | -1000 | mbar | - | 1000 | mbar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM531/P01 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-2"-P-2007.2-3BB1 | OTHER | L | 7.38 | 19 | 40 | 260 | - | - | - | - | PED Fluid Group: 1. Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FT -5054-SP
- | - | - | - | 23 | - | 1 | - | 660FC5053CA | - | TO 660 F 5001 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660F5053 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 24 | - | 1 | - | 660FC5053BA | - | TO 660 F 5001 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660F5053 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 25 | - | 1 | - | 660FAL5053CA | - | FROM 660 G 5001A/B | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | Low alarm (130) | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660F5053 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 26 | - | 1 | - | 660FAL5053BA | - | FROM 660 G 5001A/B | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | Low alarm 130 | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660F5053 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660FC5054 | - | FROM 660E5001 - 660FT5054 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660F5054 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660FE5054 | - | BIODIESEL TO TANK FARM (JET MODE) | ORIFICE | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660F5054 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | P | LP | TV3 | - | - | 0 | mbar | - | 125 | mbar | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-2"-P-2007.2-3BB1 | OTHER | L | 7.38 | 19 | 40 | 260 | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-FE -5054-SP
- | - | - | - | 2 | - | 1 | - | 660FT5058 | - | KEROSENE STRIPPER VAPOR TO 660 C 5001 | VORTEX | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 13000 | - | kg/h | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5058 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | GS RC INS 200 / Appendix 12-T13B | CI2 | NO | - | CC | - | - | 0 | kg/h | - | 13000 | kg/h | - | 659 | kg/h | - | 15824 | kg/h | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM531/P02 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-8"-P-2011.0-1BB1 | OTHER | OTHER | 0.92 | 4 | 175 | 310 | - | - | - | - | By Vendor (Note 1) | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-FT -5058-SP
- | - | - | - | 2 | - | 1 | - | 660FT5152 | - | PRODUCT FRACTIONATOR REFLUX | VORTEX | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 180 | - | m³/h | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5152 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | GS RC INS 200 / Appendix 12-T13B | CI2 | NO | - | NI (NOT INSULATED) | - | - | 0 | m³/h | - | 180 | m³/h | - | 20.6 | m³/h | - | 545 | m³/h | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM531/P03 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-6"-P-2032.1-1BB1 | OTHER | L | 7.33 | 12.5 | 41 | 120 | - | - | - | - | I | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-FT -5152-SP
- | - | - | - | 5 | - | 1 | - | 660FY5054 | - | FROM 660E5001 - 660FT5054 | SOFT CALCULATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660F5054 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660FC5055 | - | FROM 660E5001 - 660FT5055 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660F5055 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660FE5055 | - | BIODIESEL TO TANK FARM (DIESEL MODE) | ORIFICE | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660F5055 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | P | LP | TV3 | - | - | 0 | mbar | - | 250 | mbar | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-4"-P-2007.0-3BB1 | OTHER | L | 5.18 | 19 | 40 | 260 | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-FE -5055-SP
- | - | - | - | 2 | - | 1 | - | 660FT5056 | - | FRACTIONATOR BOTTOMS TO 660 E 5005 | VORTEX | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 150 | - | m³/h | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5056 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | GS RC INS 200 / Appendix 12-T13B | CI2 | NO | - | CC | - | - | 0 | m³/h | - | 150 | m³/h | - | 14.2 | m³/h | - | 249 | m³/h | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM530/P04 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-6"-P-2009.2-3BB3 | OTHER | L | 9 | 19 | 355 | 390 | - | - | - | - | I | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-FT -5056-SP
- | - | - | - | 3 | - | 1 | - | 660FT5059 | - | TO 660-C-5001 | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0209 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5059 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-420 / PART 2 FOLIO 18 | CΙ6 | NO | - | CC | - | - | 0 | mbar | - | 125 | mbar | - | -1000 | mbar | - | 1000 | mbar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM530/P05 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-3"-P-2021.1-3BB1 | KERO | L | 5.05 | 19 | 199 | 250 | - | - | - | - | PED Fluid Group: 1. Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FT -5059-SP
- | - | - | - | 1 | - | 1 | - | 660FC5056 | - | TO 660E5005 - 660FT5056 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660F5056 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | CV01 | - | 3 | - | 1 | - | 660FV5051 | - | SBC TO TANK FARM | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0209 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660F5051 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA004 | CI1/CI9 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM530/P06 | - | E10201 | 660IADM112/01 | - | - | - | - | - | - | - | - | 660-4"-P-2021.0-3BB1 | OTHER | L | 4.81 | 19 | 173 | 250 | - | - | - | - | III module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FV -5051-SP
- | - | CV01 | - | 4 | - | 1 | - | 660FV5055 | - | BIODIESEL TO TANK FARM (DIESEL MODE) | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660F5055 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA004 | CI1/CI9/CI10 | P | LP | TV3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM530/P07 | - | E10201 | 660IADM512/02 | - | - | - | - | - | - | - | - | 660-4"-P-2007.0-3BB1 | OTHER | L | 5.01 | 19 | 40 | 260 | - | - | - | - | III module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FV -5055-SP
- | - | - | - | 1 | - | 1 | - | 660FAL5057 | - | TO 660-E-5008 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660F5057 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660FC5057 | - | TO 660E5008 - 660FT5057 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660F5057 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660FE5057 | - | KEROSENE TO 660 E 5008 | ORIFICE | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660F5057 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | CC | - | - | 0 | mbar | - | 250 | mbar | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-4"-P-2016.1-3BB3 | KERO | L | 7.71 | 19 | 217 | 280 | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-FE -5057-SP
- | - | CV01 | - | 3 | - | 1 | - | 660FV5056 | 660FV5025 | DIESEL FROM 660 E 5005 | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660F5056 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA004 | CI1/CI9 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM530/P08 | - | E10201 | 660IADM515/02 | - | - | - | - | - | - | - | - | 660-6"-P-2077.0-3BB3 | OTHER | L | 8.24 | 19 | 331 | 390 | - | - | - | - | III module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FV -5056-SP
- | - | CV01 | - | 5 | - | 1 | - | 660FV5057 | - | 660 G 5002 Min flow | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660F5057 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA004 | CI1/CI9 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM530/P09 | - | E10201 | 660IADM515/03 | - | - | - | - | - | - | - | - | 660-3"-P-2016.2-3BB3 | KERO | L | - | 19 | - | 280 | - | - | - | - | III module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FV -5057-SP
- | - | - | - | 6 | - | 1 | - | 660FTS5292 | 660-FT -5292 | PROCESS FLUID TO 660E5008 | PRESSURE DP | - | - | - | N | - | L | ST1D | BPCS | S-PLC | - | 0 | 60 | - | - | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5057 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD RC INS 420 / PART 2 FOLIO 18 | CΙ6 | NO | - | CC | - | - | 0 | mbar | - | 250 | mbar | - | -1000 | mbar | - | 1000 | mbar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS530/P01 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-4"-P-2016.1-3BB3 | KERO | L | 7.71 | 19 | 217 | 280 | - | - | - | - | PED Fluid Group: 1. Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FT -5292-SP
- | - | - | - | 1 | - | 1 | - | 660FI5058 | - | TO 660C5001 - 660FT5058 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660F5058 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660FT5154 | - | TO 660-C-0001 | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 2 | - | m³/h | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5154 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CΙ6 | NO | - | NI (NOT INSULATED) | - | - | 0 | mbar | - | 125 | mbar | - | -1000 | mbar | - | 1000 | mbar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM531/P04 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-1"-P-2032.4-1BB1 | OTHER | L | 8.23 | 12.5 | 40 | 120 | - | - | - | - | PED Fluid Group: 1. Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FT -5154-SP
- | - | - | - | 1 | - | 1 | - | 660FC5059 | - | TO 660C5001 - 660FT5059 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0209 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660F5059 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660FE5059 | - | KEROSENE TO FRACTIONATOR 660 C 5001 | ORIFICE | - | - | - | - | - | L | - | BPCS/SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0209 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660F5059 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | CC | - | - | 0 | mbar | - | 125 | mbar | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-3"-P-2021.1-3BB1 | KERO | L | 5.05 | 19 | 199 | 250 | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-FE -5059-SP
- | - | CV04 | - | 4 | - | 1 | - | 660FV5059 | - | KEROSENE TO 660 C 5001 | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0209 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660F5059 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA004 | CI1/CI9 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM530/P10 | - | E10201 | 660IADM515/04 | - | - | - | - | - | - | - | - | 660-3"-P-2021.1-3BB1 | OTHER | L | 4.88 | 19 | 199 | 250 | - | - | - | - | III module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FV -5059-SP
- | - | - | - | 4 | - | 1 | - | 660LT5097 | - | 660-C-5002 | PRESSURE DP | - | - | W/T SEAL+CAPILLARY | - | - | L | ST1C | BPCS | DCS | - | 0 | 100 | - | % | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660L5097 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-430 / PART 1 FOLIO 2 | CI6 | NO | - | NI (NOT INSULATED) | Capillary 214359C-1000-STD-1576-0002-Pg5 | - | -5002.25 | mmH2O 4°C | - | -1896.95 | mmH2O 4°C | - | -10000 | mmH2O 4°C | - | 10000 | mmH2O 4°C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM530/P11 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | OTHER | OTHER | 1.1 | 4.1 | 247 | 310 | - | - | - | - | PED Group: 1 Phase Gas | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-LT -5097-SP
- | - | CV04 | - | 5 | - | 1 | - | 660UYS5059 | - | On-ff Valve 660UVS5014 | AIR SOLENOID SPRING | - | - | - | N | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0209 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660F5059 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS505/C01-C02 | - | E10207 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5059-SP
- | - | - | - | 1 | - | 1 | - | 660RO5060 | - | LP steam to 660G0002 | RESTRICT. ORIFICE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660F5060 | U | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660RO5061 | - | LP steam to 660G0102 | RESTRICT. ORIFICE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660F5061 | U | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660FAX5063 | - | DISCREPANCY ALARM | SOFT CALCULATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660F5063 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DISCREPANCY ALARM FOR 660FC5053/5270 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660RO5075 | - | WARM UP 660G5001A | RESTRICT. ORIFICE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660F5075 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | PROCESS FLUID FOR 660G5001A | - | P | LP | TV2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-3/4"-P-2009.0-3BB3 | HC | L | 9.11 | 19 | 354 | 390 | - | - | - | - | PED Fluid Group: 1. Phase: Gas | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-RO -5075-SP
- | - | - | - | 1 | - | 1 | - | 660RO5076 | - | WARM UP 660G5001B | RESTRICT. ORIFICE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660F5076 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | PROCESS FLUID FOR 660G5001B | - | P | LP | TV2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-3/4"-P-2203.0-3BB3 | HC | L | 9.11 | 19 | 354 | 390 | - | - | - | - | PED Fluid Group: 1. Phase: Gas | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-RO -5076-SP
- | - | - | - | 1 | - | 1 | - | 660FI5110 | - | NITROGEN TO FLARE HEADER | ROTAMETER | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0031-0105 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660F5110 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | 2 | kg/h | - | 24 | kg/h | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-3/4"-SB-2272.0-1CH3 | N2 | OTHER | 9 | 10 | 25 | 340 | - | - | - | - | Group: 2. Phase: Gas | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FI -5110-SP
- | - | - | - | 1 | - | 1 | - | 660RO5120 | - | PROCESS FLUID TO SB FROM 660K5001 | RESTRICT. ORIFICE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660F5120 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | PP | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-2"-P-2306.0-1BB1 | STEAM MP | OTHER | 2.7 | 8.5 | 134 | 200 | - | - | - | - | PED Fluid Group: 1. Phase: Gas | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-RO -5120-SP
- | - | - | - | 1 | - | 1 | - | 660FC5152 | - | TO 660C5001 - 660FT5152 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660F5152 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660FT5268 | - | PRODUCT FRACTIONAT. INTERNAL REFLUX | FLOW ULTRASONIC | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 60 | - | m³/h | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5268 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD RC INS 420 / PART 2 FOLIO 18 | CΙ6 | NO | - | CC | - | - | 0 | m³/h | - | 60 | m³/h | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | EXT_230V | NR | - | - | - | - | - | - | - | - | - | 660BJM531/P05 | - | E10202 | - | - | - | - | - | - | - | - | - | 660-6"-P-2004.0-3BB1 | OTHER | L | 0.9 | 4 | 213 | 390 | - | - | - | - | I | - | - | - | - | ATEX | 2 | II | - | - | - | - | - | - | - | - | 660-FT -5268-SP
- | - | CV01 | - | 22 | - | 1 | - | 660FV5053 | - | DIESEL TO 660 F 5001 Pass Inlet | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660F5053 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA004 | CI1/CI9 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM531/P06 | - | E10201 | 660IADM513/01 | - | - | - | - | - | - | - | - | 660-8"-P-2009.1-3BB3 | OTHER | L | 8.57 | 19 | 357 | 390 | - | - | - | - | III module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FV -5053-SP
- | - | - | - | 1 | - | 1 | - | 660FIC5154 | 660-FC -5154 | TO 660C0001 - 660FT5154 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660F5154 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660FE5154 | - | NAPHTHA TO 660 C 0001 (DIESEL MODE) | ORIFICE | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660F5154 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | - | - | 0 | mbar | - | 125 | mbar | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-1"-P-2032.4-1BB1 | OTHER | L | 8.23 | 12.5 | 40 | 120 | - | - | - | - | II | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-FE -5154-SP
- | - | CV01 | - | 4 | - | 1 | - | 660FV5054 | - | BIODIESEL TO TANK FARM (JET MODE) | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660F5054 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA004 | CI1/CI9/CI10 | P | LP | TV3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM531/P07 | - | E10201 | 660IADM512/01 | - | - | - | - | - | - | - | - | 660-2"-P-2007.2-3BB1 | OTHER | L | 7.21 | 19 | 40 | 260 | - | - | - | - | III module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FV -5054-SP
- | - | CV01 | - | 3 | - | 1 | - | 660FV5152 | - | Product Fractionator Reflux | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660F5152 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA004 | CI1/CI9 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM531/P08 | - | E10201 | 660IADM513/02 | - | - | - | - | - | - | - | - | 660-6"-P-2032.1-1BB1 | OTHER | L | 7.26 | 12.5 | 41 | 120 | - | - | - | - | III module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FV -5152-SP
- | - | - | - | 1 | - | 1 | - | 660FAL5155 | - | TO 660-C-0001 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660F5155 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660FC5155 | - | TO 660C0001 - 660FT5155 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660F5155 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660FE5155 | - | NAPHTHA TO 660 C 0001 (JET MODE) | ORIFICE | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660F5155 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | - | - | 0 | mbar | - | 250 | mbar | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-2"-P-2032.3-1BB1 | OTHER | L | 7.29 | 12.5 | 40 | 120 | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-FE -5155-SP
- | - | - | - | 4 | - | 1 | - | 660FT5155 | - | TO 660-C-0001 | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 13 | - | m³/h | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5155 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-420 / PART 2 FOLIO 18 | CΙ6 | NO | - | NI (NOT INSULATED) | - | - | 0 | mbar | - | 250 | mbar | - | -1000 | mbar | - | 1000 | mbar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM538/P01 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-2"-P-2032.3-1BB1 | OTHER | L | 7.29 | 12.5 | 40 | 120 | - | - | - | - | PED Fluid Group: 1. Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FT -5155-SP
- | - | - | - | 2 | - | 1 | - | 660FT5301 | - | FUEL GAS TO 660-F 5001 | CORIOLIS | - | - | ALIM EXT | - | - | L | ST1C | BPCS | DCS | - | 0 | 1300 | - | kg/h | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5301 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | GS RC INS 200 / Appendix 12-T11D | CI2 | NO | - | CC | - | - | 0 | kg/h | - | 1300 | kg/h | - | 0 | kg/h | - | 1830 | kg/h | - | - | - | - | - | - | AI11 | EXT_230V | NR | - | - | - | - | - | - | - | - | - | 660BJM538/P02 | - | E10202 | - | - | - | - | - | - | - | - | - | 660-4"-FG-2095.0-1KB2 | GN | OTHER | 2.8 | 3.5 | 41 | 75 | - | - | - | - | I | - | - | - | - | ATEX | - | IIC | - | - | - | - | - | - | - | - | 660-FT -5301-SP
- | - | - | - | 1 | - | 1 | - | 660FAL5156 | - | TO 660-C-5001 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660F5156 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660FC5156 | - | TO 660C5001 - 660FT5156 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660F5156 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660FE5156 | - | PRODUCT FRACTIONATOR OVERHEAD PUMPS DISCHARGE | ORIFICE | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660F5156 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | - | - | 0 | mbar | - | 250 | mbar | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2032.1-1BB1 | OTHER | L | 8.35 | 12.5 | 40 | 120 | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-FE -5156-SP
- | - | CV04 | - | 4 | - | 1 | - | 660FV5154 | - | NAPHTHA TO 660 C 0001 (DIESEL MODE) | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660F5154 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA004 | CI1/CI9 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM531/P09 | - | E10201 | 660IADM518/01 | - | - | - | - | - | - | - | - | 660-1"-P-2032.4-1BB1 | OTHER | L | 8.06 | 12.5 | 40 | 120 | - | - | - | - | III module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FV -5154-SP
- | - | CV01 | - | 5 | - | 1 | - | 660FV5156 | - | MIN FLOW TO 660 D 5001 | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660F5156 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA004 | CI1/CI9 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM531/P10 | - | E10201 | 660IADM513/03 | - | - | - | - | - | - | - | - | 660-4"-P-2032.2-1BB1 | OTHER | L | 8.29 | 12.5 | 40 | 120 | - | - | - | - | III module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FV -5156-SP
- | - | - | - | 1 | - | 1 | - | 660FI5157 | - | TO FRACTIONATOR OFFGAS LPG RECOVERY - 660FT5157 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | 0 | 1300 | - | kg/h | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660F5157 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660FT5157 | - | TO FRACTIONATOR OFFGAS LPG RECOVERY | VORTEX | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5157 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | GS RC INS 200 / Appendix 12-T13B | CI2 | NO | - | NI (NOT INSULATED) | - | - | 0 | kg/h | - | 1300 | kg/h | - | 115 | kg/h | - | 4550 | kg/h | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM536/P01 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-3"-P-2037.1-1BB1 | OTHER | OTHER | 6.2 | 8 | 40 | 180 | - | - | - | - | I | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-FT -5157-SP
- | - | - | - | 1 | - | 1 | - | 660FC5158 | - | TO 660E5008 - 660FT5158 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0216 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660F5158 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660FT5158 | - | KEROSENE TO 660 E 5008 | VORTEX | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 70 | - | m³/h | 214359C-6602-PID-0021-0216 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5158 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | GS RC INS 200 / Appendix 12-T13B | CI2 | NO | - | CC | - | - | 0 | m³/h | - | 70 | m³/h | - | 5.62 | m³/h | - | 143 | m³/h | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM534/P01 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-4"-P-2016.1-3BB3 | KERO | L | 7.3 | 19 | 217 | 280 | - | - | - | - | I | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-FT -5158-SP
- | - | - | - | 1 | - | 1 | - | 660FT5164 | - | API PLAN PUMP 660G5001A | ROTAMETER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5164 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | CI2 | - | - | NI (NOT INSULATED) | - | - | - | mbar | - | - | - | - | - | mbar | - | - | - | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM534/P02 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660FT5218 | - | API PLAN PUMP 660G5001B | ROTAMETER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5218 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | CI2 | - | - | NI (NOT INSULATED) | - | - | - | mbar | - | - | - | - | - | mbar | - | - | - | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM534/P03 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660FT5251 | - | FROM 660-E-0004A | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 16 | - | m³/h | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5251 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-420 / PART 2 FOLIO 18 | CΙ6 | NO | - | NI (NOT INSULATED) | - | - | 0 | mbar | - | 125 | mbar | - | -1000 | mbar | - | 1000 | mbar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM534/P04 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-6"-P-2043.0-1BB1 | OTHER | L | 7.9 | 11.5 | 40 | 122 | - | - | - | - | PED Fluid Group: 1. Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FT -5251-SP
- | - | - | - | 1 | - | 1 | - | 660FC5251 | - | FROM 660E0004A - 660FT5251 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - |  | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660F5251 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660FE5251 | - | NAPHTHA TO BATTERY LIMIT (JET MODE) | ORIFICE | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660F5251 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | - | - | 0 | mbar | - | 125 | mbar | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2043.1-1BB1 | OTHER | L | 7.9 | 11.5 | 40 | 122 | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-FE -5251-SP
- | - | - | - | 3 | - | 1 | - | 660FT5252 | - | FROM 660-E-0004A | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 3.6 | - | m³/h | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5252 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CΙ6 | NO | - | NI (NOT INSULATED) | - | - | 0 | mbar | - | 250 | mbar | - | -1000 | mbar | - | 1000 | mbar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM534/P05 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-1 1/2"-P-2043.0-1BB1 | OTHER | L | 8.46 | 11.5 | 40 | 122 | - | - | - | - | PED Fluid Group: 1. Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FT -5252-SP
- | - | - | - | 3 | - | 1 | - | 660FT5253 | - | TO 660 E 5008 | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 75 | - | m³/h | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5253 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-420 / PART 2 FOLIO 18 | CΙ6 | NO | - | CC | - | - | 0 | mbar | - | 250 | mbar | - | -1000 | mbar | - | 1000 | mbar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM534/P06 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-6"-P-2046.0-1BB1 | OTHER | L | 8.33 | 11.5 | 118 | 160 | - | - | - | - | PED Fluid Group: 1. Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FT -5253-SP
- | - | - | - | 5 | - | 1 | - | 660FY5251 | - | FROM 660E0004A - 660FT5251 | SOFT CALCULATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660F5251 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660FC5252 | - | FROM 660E0004A - 660FT5252 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660F5252 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660FE5252 | - | NAPHTHA TO BATTERY LIMIT (DIESEL MODE) | ORIFICE | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660F5252 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | - | - | 0 | mbar | - | 250 | mbar | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-1-1/2"-P-2043.0-1BB1 | OTHER | L | 8.46 | 11.5 | 40 | 122 | - | - | - | - | Art 4.3, See note 1 | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-FE -5252-SP
- | - | - | - | 1 | - | 1 | - | 660FT5264 | - | API PLAN PUMP 660G5001A | ROTAMETER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5264 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | - | - | - | CC | - | - | - | mbar | - | - | - | - | - | mbar | - | - | - | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM534/P07 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660FT5418 | - | API PLAN PUMP 660G5001A | ROTAMETER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5418 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | - | - | - | CC | - | - | - | mbar | - | - | - | - | - | mbar | - | - | - | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM534/P08 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660FC5253 | - | TO 660E5008 - 660FT5253 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660F5253 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660FE5253 | - | DEBUTANIZER BOTTOMS TO REBOILER | ORIFICE | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660F5253 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | CC | - | - | 0 | mbar | - | 250 | mbar | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2046.0-1BB1 | OTHER | L | 8.33 | 11.5 | 118 | 160 | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-FE -5253-SP
- | - | CV01 | - | 3 | - | 1 | - | 660FV5158 | - | KEROSENE FROM 660 E 5008 | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0216 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660F5158 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA004 | CI1/CI9 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM534/P09 | - | E10201 | 660IADM517/01 | - | - | - | - | - | - | - | - | 660-4"-P-2016.5-3BB1 | OTHER | L | 6.55 | 19 | 170 | 280 | - | - | - | - | III module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FV -5158-SP
- | - | CV01 | - | 4 | - | 1 | - | 660FV5251 | - | NAPTHA FROM 660 E 0004A (JET MODE) | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660F5251 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA004 | CI1/CI9 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM534/P10 | - | E10201 | 660IADM110/01 | - | - | - | - | - | - | - | - | 660-6"-P-2043.1-1BB1 | OTHER | L | 7.73 | 11.5 | 40 | 122 | - | - | - | - | III module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FV -5251-SP
- | - | - | - | 1 | - | 1 | - | 660FI5254 | - | FROM 660D0004 - 660FT5254 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660F5254 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660FT5254 | - | OFF GAS TO LPG RECOVERY | CORIOLIS | - | - | ALIM EXT | - | - | L | ST1C | BPCS | DCS | - | 0 | 2500 | - | kg/h | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5254 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | GS RC INS 200 / Appendix 12-T11D | CI2 | P | LP | TV3 | - | - | 0 | kg/h | - | 2500 | kg/h | - | 0 | kg/h | - | 4720 | kg/h | - | - | - | - | - | - | AI11 | EXT_230V | NR | - | - | - | - | - | - | - | - | - | 660BJM535/P01 | - | E10202 | - | - | - | - | - | - | - | - | - | 660-6"-P-2050.0-1BB1 | OTHER | OTHER | 3.95 | 5.5 | 40 | 160 | - | - | - | - | I | - | - | - | - | ATEX | - | IIC | - | - | - | - | - | - | - | - | 660-FT -5254-SP
- | - | - | - | 1 | - | 1 | - | 660FAL5256 | - | TO 660 C 0001 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660F5256 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660FC5256 | - | TO 660C0001 - 660FT5256 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660F5256 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660FE5256 | - | DEBUTANIZER OVERHEAD PUMPS DISCHARGE | ORIFICE | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660F5256 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | - | - | 0 | mbar | - | 250 | mbar | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-2"-P-2408.0-3BB1 | HC | L | 19.46 | 23 | 40 | 120 | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-FE -5256-SP
- | - | - | - | 4 | - | 1 | - | 660FT5256 | - | TO 660 C 0001 | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 16 | - | m³/h | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5256 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-420 / PART 5 FOLIO 4 | CΙ2 | NO | - | NI (NOT INSULATED) | - | - | 0 | mbar | - | 250 | mbar | - | -1000 | mbar | - | 1000 | mbar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM535/P02 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-2"-P-2408.0-3BB1 | HC | L | 19.46 | 23 | 40 | 120 | - | - | - | - | PED Fluid Group: 1. Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FT -5256-SP
- | - | - | - | 5 | - | 1 | - | 660FT5296 | - | PROCESS FLUID T 660-E-5008 | PRESSURE DP | - | - | - | - | - | L | ST1C | SIS | DCS | - | 0 | 100 | - | m³/h | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5295 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-420 / PART 2 FOLIO 18 | CΙ6 | NO | - | NI (NOT INSULATED) | - | - | 0 | mbar | - | 125 | mbar | - | -1000 | mbar | - | 1000 | mbar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM535/P03 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-6"-P-25.1-1BB1 | HC | L | 8.35 | 11.5 | 118 | 160 | - | - | - | - | PED Fluid Group: 1. Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FT -5296-SP
- | - | - | - | 3 | - | 1 | - | 660FT5258 | - | TO 660 F 5001 | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5258 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CC | - | - | 0 | mbar | - | 250 | mbar | - | - | mbar | - | - | - | - | - | - | - | - | - | - | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-8"-P-2009.3-3BB3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660FE5259 | - | LP STEAM FROM OSBL | ORIFICE | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0041-0002 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660F5259 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | CC | - | - | 70 | mbar | - | 250 | mbar | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-VB-2066.0-1BS1 | STEAM LP | S | 3.9 | 5.5 | 160 | 200 | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-FE -5259-SP
- | - | - | - | 2 | - | 1 | - | 660FI5259 | - | FUEL GAS FROM OSBL - 660FT5259AB | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0041-0002 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660F5259 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660FT5259A | - | LP STEAM FROM OSBL | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 1100 | - | kg/h | 214359C-6602-PID-0041-0002 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5259 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD RC INS 420 / PART 4 FOLIO 3 | CΙ2 | NO | - | CC | - | - | 0 | mbar | - | 70 | mbar | - | -1000 | mbar | - | 1000 | mbar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM536/P02 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-6"-VB-2066.0-1BS1 | STEAM LP | S | 3.9 | 5.5 | 160 | 200 | - | - | - | - | PED Fluid Group: 1. Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FT -5259-SP
- | - | - | - | 4 | - | 1 | - | 660FY5259 | - | LP STEAM FROM OSBL - 660FT5259AB | I/P CONVERTER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0041-0002 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660F5259 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | CC | - | - | - | mbar | - | - | - | - | - | mbar | - | - | - | - | - | - | - | - | - | - | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660FT5259B | 660-FE -5259B | LP STEAM FROM OSBL | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 2056 | - | kg/h | 214359C-6602-PID-0041-0002 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5259 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD RC INS 420 / PART 4 FOLIO 3 | CΙ2 | NO | - | CC | - | - | 0 | mbar | - | 250 | mbar | - | -1000 | mbar | - | 1000 | mbar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM536/P03 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-6"-VB-2066.0-1BS1 | STEAM LP | S | 3.9 | 5.5 | 160 | 200 | - | - | - | - | PED Fluid Group: 1. Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FE -5259B-SP
- | - | - | - | 1 | - | 1 | - | 660FE5260 | - | MP STEAM FROM OSBL | ORIFICE | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0041-0002 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660F5260 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | mbar | - | 125 | mbar | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660FI5260 | - | FUEL GAS FROM OSBL | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0041-0002 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660F5260 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660FT5260 | - | MP STEAM FROM OSBL | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0041-0002 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5260 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-420 / PART 4 FOLIO 2 | CI2 | NO | - | NI (NOT INSULATED) | - | - | 0 | mbar | - | 125 | mbar | - | - | mbar | - | - | - | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 600-3"-VM-1012.0-3BS1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | CV01 | - | 4 | - | 1 | - | 660FV5252 | - | NAPHTHA FROM 660 E 0004A (DIESEL MODE) | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660F5252 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA004 | CI1/CI9 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM534/P11 | - | E10201 | 660IADM110/02 | - | - | - | - | - | - | - | - | 660-1 1/2"-P-2043.0-1BB1 | OTHER | L | 8.29 | 11.5 | 40 | 122 | - | - | - | - | III module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FV -5252-SP
- | - | CV01 | - | 22 | - | 1 | - | 660FV5270 | 660-FV -5258 | DIESEL TO 660 F 5001 Pass Inlet | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660F5270 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA004 | CI1/CI9 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM531/P11 | - | E10201 | 660IADM513/04 | - | - | - | - | - | - | - | - | 660-8"-P-2009.3-3BB3 | OTHER | L | 8.57 | 19 | 357 | 390 | - | - | - | - | III module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FV -5270-SP
- | - | - | - | 2 | - | 1 | - | 660FI5268 | - | FROM 660C5001 - 660FT5268 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660F5268 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | L | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660FE5268 | - | PRODUCT FRACTIONAT. INTERNAL REFLUX | ANNUBAR | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660F5268 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-4"-P-2004.0-3BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660FE5269 | - | NATURAL GAS TO 660 D 5001/0004 | ORIFICE | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0041-0002 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660F5269 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | - | - | 50 | mbar | - | 250 | mbar | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-4"-FG-2081.0-1BB1 | GN | OTHER | 3 | 3.5 | 41 | 75 | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-FE -5269-SP
- | - | - | - | 2 | - | 1 | - | 660FI5269 | - | FUEL GAS FROM OSBL - 660FT5259AB | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0041-0002 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660F5269 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660FT5269A | - | FUEL GAS FROM OSBL | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 800 | - | kg/h | 214359C-6602-PID-0041-0002 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5269 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-420 / PART 3 FOLIO 4 | CΙ2 | NO | - | NI (NOT INSULATED) | - | - | 0 | mbar | - | 50 | mbar | - | -1000 | mbar | - | 1000 | mbar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM536/P04 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-3"-FG-2081.0-1BB1 | GN | OTHER | 3 | 3.5 | 41 | 75 | - | - | - | - | PED Fluid Group: 1. Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FT -5269-SP
- | - | - | - | 4 | - | 1 | - | 660FY5269 | - | FUEL GAS FROM OSBL - 660FT5259AB | I/P CONVERTER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0041-0002 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660F5269 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | mbar | - | - | - | - | - | mbar | - | - | - | - | - | - | - | - | - | - | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660FT5275 | - | API PLAN PUMP 660G5002A | ROTAMETER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5275 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | - | - | - | CC | - | - | - | mbar | - | - | - | - | - | mbar | - | - | - | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM536/P05 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660FE5270 | 660-FE -5258 | INLET PASS TO REBOILER 660 F 5001 | ORIFICE | - | - | - | - | - | L | - | BPCS/SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660F5270 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | CC | - | - | 0 | mbar | - | 250 | mbar | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-8"-P-2009.3-3BB3 | OTHER | L | 8.77 | 19 | 357 | 390 | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-FE -5270-SP
- | - | - | - | 2 | - | 1 | - | 660FTS5053A | - | FROM 660 G 5001A/B | PRESSURE DP | - | - | - | - | - | L | ST1D | BPCS/SIS | CONV | - | 0 | 265 | - | m³/h | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5053 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-420 / PART 2 FOLIO 6 | CΙ6 | P | LP | TV2 | STD RC INS 220 / FOLIO 30 | - | 0 | mbar | - | 250 | mbar | - | -1000 | mbar | - | 1000 | mbar | - | - | - | - | - | - | - | - | NR | - | 660FTS5053A | - | - | - | - | - | - | - | 660BJMS531/P01 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-8"-P-2009.1-3BB3 | OTHER | L | 8.77 | 19 | 357 | 390 | - | - | - | - | PED Fluid Group: 1. Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FTS -5053A-SP
- | - | - | - | 3 | - | 1 | - | 660FTS5053B | - | FROM 660 G 5001A/B | PRESSURE DP | - | - | - | - | - | L | ST1D | BPCS/SIS | CONV | - | 0 | 265 | - | m³/h | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5053 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-420 / PART 2 FOLIO 6 | CΙ6 | P | LP | TV2 | STD RC INS 220 / FOLIO 30 | - | 0 | mbar | - | 250 | mbar | - | -1000 | mbar | - | 1000 | mbar | - | - | - | - | - | - | - | - | NR | - | 660FTS5053B | - | - | - | - | - | - | - | 660BJMS531/P02 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-8"-P-2009.1-3BB3 | OTHER | L | 8.77 | 19 | 357 | 390 | - | - | - | - | PED Fluid Group: 1. Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FTS -5053B-SP
- | - | - | - | 4 | - | 1 | - | 660FTS5053C | - | FROM 660 G 5001A/B | PRESSURE DP | - | - | - | - | - | L | ST1D | BPCS/SIS | CONV | - | 0 | 265 | - | m³/h | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5053 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-420 / PART 2 FOLIO 6 | CΙ6 | P | LP | TV2 | STD RC INS 220 / FOLIO 30 | - | 0 | mbar | - | 250 | mbar | - | -1000 | mbar | - | 1000 | mbar | - | - | - | - | - | - | - | - | NR | - | 660FTS5053C | - | - | - | - | - | - | - | 660BJMS540/P01 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-8"-P-2009.1-3BB3 | OTHER | L | 8.77 | 19 | 357 | 390 | - | - | - | - | PED Fluid Group: 1. Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FTS -5053C-SP
- | - | - | - | 5 | - | 1 | - | 660FTS5270AA | 660-FAL -5270AA | TO 660F5001 - 660FTS5270ABC | OUTPUT CONVERTER | - | - | - | N | - | ITR | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5270 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660FTS5270BA | 660-FAL -5270BA | TO 660F5001 - 660FTS5270ABC | OUTPUT CONVERTER | - | - | - | N | - | ITR | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5270 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 1 | - | 660FTS5270CA | 660-FAL -5270CA | TO 660F5001 - 660FTS5270ABC | OUTPUT CONVERTER | - | - | - | N | - | ITR | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5270 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 1 | - | 660FTS5270AB | - | TO 660F5001 - 660FTS5270ABC | OUTPUT CONVERTER | - | - | - | N | - | ITR | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5270 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | EXT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 9 | - | 1 | - | 660FTS5270BB | - | TO 660F5001 - 660FTS5270ABC | OUTPUT CONVERTER | - | - | - | N | - | ITR | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5270 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | EXT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 10 | - | 1 | - | 660FTS5270CB | - | TO 660F5001 - 660FTS5270ABC | OUTPUT CONVERTER | - | - | - | N | - | ITR | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5270 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | EXT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 11 | - | 1 | - | 660FI5270A | 660-FI -5270AA | TO 660F5001 - 660FTS5270ABC | INDICATION | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660F5270 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 12 | - | 1 | - | 660FI5270B | 660-FI -5270BA | TO 660F5001 - 660FTS5270ABC | INDICATION | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660F5270 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 13 | - | 1 | - | 660FI5270C | 660-FI -5270CA | TO 660F5001 - 660FTS5270ABC | INDICATION | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660F5270 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 14 | - | 1 | - | 660FSLL5270AA | - | TO 660F5001 - 660FTS5270ABC | SOFT THERSHOLD | - | - | - | N | - | ITR | ST1D | BPCS/SIS | S-PLC | - | - | - | Low Low Aalarm (91) | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660F5270 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 15 | - | 1 | - | 660FSLL5270BA | - | TO 660F5001 - 660FTS5270ABC | SOFT THERSHOLD | - | - | - | N | - | ITR | ST1D | BPCS/SIS | S-PLC | - | - | - | Low Low Aalarm (91) | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660F5270 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 16 | - | 1 | - | 660FSLL5270CA | - | TO 660F5001 - 660FTS5270ABC | SOFT THERSHOLD | - | - | - | N | - | ITR | ST1D | BPCS/SIS | S-PLC | - | - | - | Low Low Aalarm (91) | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660F5270 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 17 | - | 1 | - | 660FALL5270 | - | TO 660F5001 - 660FTS5270ABC | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | Low Low Aalarm (128) | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660F5270 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 18 | - | 1 | - | 660FAX5270 | - | TO 660 F 5001 | SOFT CALCULATION | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660F5270 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 19 | - | 1 | - | 660FSL5270 | - | TO 660F5001 - 660FTS5270ABC | SOFT THERSHOLD | - | - | - | N | - | ITR | ST1C | BPCS/SIS | DCS | - | - | - | low Alarm (130) | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660F5270 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 20 | - | 1 | - | 660FAL5270 | - | TO 660F5001 - 660FTS5270ABC | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | low Alarm (135) | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660F5270 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 21 | - | 1 | - | 660FC5270 | 660-FC -5258 | TO 660F5001 - 660FTS5270ABC | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660F5270 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660LT5095 | - | PRODUCT FRACTIONATOR KEROSENE DRAW TRAY | PRESSURE DP | - | - | W/T SEAL+CAPILLARY | N | - | L | ST1C | BPCS | DCS | - | 0 | 100 | - | % | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660L5095 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-430 / PART 1 FOLIO 2 | CI6 | NO | - | CC | - | - | -1309 | mmH2O 4°C | - | -457.24 | mmH2O 4°C | - | -10000 | mmH2O 4°C | - | 10000 | mmH2O 4°C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM531/P12 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | OTHER | OTHER | 0.8 | 4 | 213 | 390 | - | - | - | - | PED Group: 1 Phase Gas | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-LT -5095-SP
- | - | - | - | 23 | - | 1 | - | 660FC5270BA | - | TO 660 F 5001 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660F5270 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 24 | - | 1 | - | 660FC5270CA | - | TO 660 F 5001 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660F5270 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660FT5276 | - | API PLAN PUMP 660G5002b | ROTAMETER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | FR-GPS-660-2-TENV-660G0002 MMS | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5276 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | CI2 | - | - | NI (NOT INSULATED) | - | - | - | mbar | - | - | - | - | - | mbar | - | - | - | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM536/P06 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660LT5191 | - | 660-D-5002 | PRESSURE DP | - | - | W/T SEAL+CAPILLARY | - | - | L | ST1C | BPCS | DCS | - | 0 | 100 | - | % | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660L5191 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-430 / PART 1 FOLIO 2 | CI6 | NO | - | NI (NOT INSULATED) | - | - | -1177 | mmH2O 4°C | - | -485.78 | mmH2O 4°C | - | -10000 | mmH2O 4°C | - | 10000 | mmH2O 4°C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM536/P07 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | OTHER | OTHER | 6.3 | 8 | 40 | 180 | - | - | - | - | PED Group: 1 Phase Gas | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-LT -5191-SP
- | - | - | - | 2 | - | 1 | - | 660FI5292 | - | FLOW TO 660E5008 - 660FTS5292 | FLOW INDICATOR | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660F5292 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INDICATION PROCESS FLUID TO 660E5008 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660FSLL5292 | - | FLOW TO 660E5008 - 660FTS5292 | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | 22 | Am³/h | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660F5292 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INDICATIONPROCESS FLUID TO 660E5008 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660FAX5292 | - | FLOW TO 660E5008 - 660FTS5292 | SOFT CALCULATION | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660F5292 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ALARM PROCESS FLUID TO 660E5008 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660FTS5295 | - | PROCESS FLUID T 660-E-5008 | PRESSURE DP | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | 0 | 100 | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5295 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD RC INS 420 / PART 2 FOLIO 18 | CΙ6 | NO | - | NI (NOT INSULATED) | - | - | 0 | mbar | - | 125 | mbar | - | -1000 | mbar | - | 1000 | mbar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS534/P01 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-6"-P-25.1-1BB1 | HC | L | 8.35 | 11.5 | 118 | 160 | - | - | - | - | PED Fluid Group: 1. Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FTS -5295-SP
- | - | - | - | 2 | - | 1 | - | 660FE5295 | - | DEBUTANIZER BOTTOM PUMP DISCHARGE | ORIFICE | - | - | - | - | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660F5295 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | - | - | 0 | mbar | - | 125 | mbar | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-25.1.TIP3132-1BB1 | HC | L | 8.35 | 11.5 | 118 | 160 | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-FE -5295-SP
- | - | - | - | 3 | - | 1 | - | 660FI5295 | - | PROCESS FLUID T 660E5008 -660FTS5295 | INDICATION | - | - | - | N | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660F5295 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TO 660K5004 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660FSLL5295 | - | PROCESS FLUID T 660E5008 -660FTS5295 | ALARM | - | - | - | N | - | CRD | SdC | SIS | S-PLC | - | - | - | 37 | m³/h | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660F5295 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TO 660K5004 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | CV01 | - | 5 | - | 1 | - | 660FV5256 | - | MIN FLOW TO 660 D 0004 | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660F5256 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA004 | CI1/CI9 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM535/P04 | - | E10201 | 660IADM516/01 | - | - | - | - | - | - | - | - | 660-2"-P-2051.0-3BB1 | OTHER | L | 19.58 | 23 | 40 | 120 | - | - | - | - | III module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FV -5256-SP
- | - | - | - | 2 | - | 1 | - | 660FI5296 | - | PROCESS FLUID T 660E5008 -660FT5296 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660F5296 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TO 660K5004 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660FAL5296 | - | PROCESS FLUID T 660E5008 -660FT5296 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | Low-Low alarm (22) | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660F5296 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TO 660K5004 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660FAX5296 | - | PROCESS FLUID T 660E5008 -660FT5296 | SOFT CALCULATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660F5296 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TO 660K5004 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660FC5301 | - | TO 660F5001 - 660FT5301 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660F5301 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | CV04 | - | 5 | - | 1 | - | 660FV5155 | - | NAPHTHA TO 660 C 0001 (JET MODE) | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660F5155 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA004 | CI1/CI9 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM538/P03 | - | E10201 | 660IADM518/02 | - | - | - | - | - | - | - | - | 660-2"-P-2032.3-1BB1 | OTHER | L | 7.12 | 12.5 | 40 | 120 | - | - | - | - | III module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FV -5155-SP
- | - | - | - | 3 | - | 1 | - | 660FE5301 | - | FUEL GAS TO 660 F 5001 | ORIFICE | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660F5301 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-4"-FG-2095.0-1KB2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660FI5301 | - | TO 660F5001 - 660FT5301 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660F5301 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660FT5302 | - | TO 660 F 5001 | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 15500 | - | m3/h | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | Alarm LL: 4500 | - | - | - | 3 | 660F5302 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | - | NO | - | NI (NOT INSULATED) | - | - | 0 | mbar | - | 15500 | mbar | - | - | mbar | - | - | - | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM532/P04 | - | E10201 | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660FE5302 | - | AIR SUPPLY TO 660 K 5004 | VENTURI TUBE | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660F5302 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660FC5302 | - | TO 660 F 5001 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660F5302 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660FY5302A | - | TO 660 F 5001 | SOFT CALCULATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660F5302 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660FY5302 | - | TO 660 F 5001 | SOFT CALCULATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660F5302 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660FV5302 | - | TO 660 F 5001 | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660F5302 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 1 | - | 660FI5302 | - | TO 660 F 5001 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660F5302 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 1 | - | 660FAL5302 | - | TO 660 F 5001 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | Law Alarm (4,670) | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660F5302 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660FE5319 | - | FROM 660K5004 | ORIFICE | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660F5319 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TO 660K5004 | CI1 | HOLD | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660FTS5319 | 660-FT -5319 | FROM 660K5004 | PRESSURE DP | - | - | - | N | - | L | ST1D | BPCS | S-PLC | - | 0 | 15500 |  | m3/h | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | Alarm L: 5000 | - | - | - | 3 | 660F5319 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TO 660K5004 | - | NO | - | NI (NOT INSULATED) | - | - | 0 | mbar | - | 15500 | mbar | - | - | mbar | - | - | - | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS538/P01 | - | E10201 | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660FI5319 | - | FROM 660K5004 - 660FTS5319 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660F5319 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660FSLL5319 | - | FROM 660K5004 - 660FTS5319 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | S-PLC | - | - | - | Low Alarm (3,850) | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660F5319 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660PDT5084 | 660FT5084 | PRODUCT FRACTIONATOR | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 4 | - | bar | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5084 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-411 / PART 2 FOLIO 5 | CI2 | P | LP | TV2 | STD RC INS 220 / FOLIO 26 | - | 0 | bar | - | 4 | bar | - | -5000 | mbar | - | 5000 | mbar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM532/P05 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-20"-P-2010.0-3BB3 | OTHER | OTHER | 1.7 | 5.2 | 361 | 390 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PDT -5084-SP
- | - | - | - | 3 | - | 1 | - | 660PT5308 | - | PRODUCT FRACTIONATOR REBOILER | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -0.5 | 0.5 | - | mbar Gage | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5308 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 3 | HOLD | NO | - | NI (NOT INSULATED) | - | - | -0.5 | mbar | Gage | 0.5 | mbar | Gage | -50 | mbar | - | 50 | mbar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM532/P06 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | FG | OTHER | 0 | 2.5 | 374 | 1100 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PT -5308-SP
- | - | - | - | 1 | - | 1 | - | 660PT5309 | 660-PG -5309 | 660K5001 FLUE GAS PRESSURE | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -0.5 | 0.5 | - | mbar Gage | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5309 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 3 | HOLD | NO | - | NI (NOT INSULATED) | - | - | -0.5 | mbar | Gage | 0.5 | mbar | Gage | -50 | mbar | - | 50 | mbar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM537/P01 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | FG | OTHER | 0 | 2.5 | 845 | 1100 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PT -5309-SP
- | - | - | - | 1 | - | 1 | - | 660PT5314 | - | COMBUSTION AIR TO PRODUCT FRACTIONATOR REBOILER | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 30 | - | mbar Gage | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5314 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 2 | CI2 | NO | - | CC | - | - | 0 | mbar | Gage | 30 | mbar | Gage | -50 | mbar | Gage | 50 | mbar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM537/P02 | - | E10201 | - | - | - | - | - | - | - | - | - | DUCTS | OTHER | OTHER | 0.01 | 2.5 | 310 | 330 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PG -5314-SP
- | - | CV01 | - | 4 | - | 1 | - | 660FV5253 | - | NAPHTHA TO 660 E 5008 | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660F5253 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA004 | CI1/CI9 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM534/P12 | - | E10201 | 660IADM517/02 | - | - | - | - | - | - | - | - | 660-6"-P-2046.0-1BB1 | OTHER | L | 8.16 | 11.5 | 118 | 160 | - | - | - | - | III module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FV -5253-SP
- | - | - | - | 1 | - | 1 | - | 660FSL5500 | - | 660 K 5001 COMPRESSOR | LOW-FLOW SWITCH | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0,41 | 3,4 | - | m³/h | P22201-100-02 | - | - | - | - | 660-2-Fractionation | Alarm L: 1.6 | - | - | - | 7 | 660F5500 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | - | - | - | - | - | - | - | - | - | - | - | - | 0.41 | m³/h | - | 3.4 | m³/h | - | - | - | - | - | - | AI11 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM515/P01 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660FA5500 | - | 660 K 5001 COMPRESSOR | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660F5500 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660FAL5500 | - | 660 K 5001 COMPRESSOR | LOW-FLOW ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | Low Alarm (1,6) | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660F5500 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660RO5550 | - | 660 K 5001 COMPRESSOR | RESTRICT. ORIFICE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660F5550 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660RO5551 | - | 660 K 5001 COMPRESSOR | RESTRICT. ORIFICE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660F5551 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660RO5552 | - | 660 K 5001 COMPRESSOR | RESTRICT. ORIFICE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660F5552 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660RO5553 | - | 660 K 5001 COMPRESSOR | RESTRICT. ORIFICE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660F5553 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660RO5554 | - | 660 K 5001 COMPRESSOR | RESTRICT. ORIFICE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660F5554 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660RO5555 | - | 660 K 5001 COMPRESSOR | RESTRICT. ORIFICE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660F5555 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660RO5556 | - | 660 K 5001 COMPRESSOR | RESTRICT. ORIFICE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660F5556 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660RO5557 | - | 660 K 5001 COMPRESSOR | RESTRICT. ORIFICE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660F5557 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660RO5558 | - | 660 K 5001 COMPRESSOR | RESTRICT. ORIFICE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660F5558 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660RO5559 | - | 660 K 5001 COMPRESSOR | RESTRICT. ORIFICE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660F5559 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660RO5560 | - | 660 K 5001 COMPRESSOR | RESTRICT. ORIFICE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660F5560 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660RO5561 | - | 660 K 5001 COMPRESSOR | RESTRICT. ORIFICE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660F5561 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660RO5562 | - | 660 K 5001 COMPRESSOR | RESTRICT. ORIFICE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660F5562 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660RO5563 | - | 660 K 5001 COMPRESSOR | RESTRICT. ORIFICE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660F5563 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660RO5564 | - | 660 K 5001 COMPRESSOR | RESTRICT. ORIFICE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660F5564 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660RO5565 | - | 660 K 5001 COMPRESSOR | RESTRICT. ORIFICE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660F5565 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660FSH5991 | - | 660-2 ALARM F&G | HIGH-FLOW SWITCH | - | - | - | N | - | L | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 7 | 660F5991 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJGS102/P07 | - | E11204 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660FSHH5991 | - | 660-2 ALARM F&G | SOFT THERSHOLD | - | - | - | N | - | ITR | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660F5991 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660FSH5992 | - | 660-2 ALARM F&G | HIGH-FLOW SWITCH | - | - | - | - | - | L | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 7 | 660F5992 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | E11204 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660FSHH5992 | - | 660-2 ALARM F&G | SOFT THERSHOLD | - | - | - | N | - | ITR | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660F5992 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 1 | - | 1 | - | 660HS0002D | 660-HS -0002AD | 660-G-0002 LOCAL START | PB | - | - | NORMALLY OPEN | - | - | L | - | BPCS/SIS | MOT | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G0002 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 3 | - | 1 | - | 660HS0002A | 660-HS -0002AA | 660-G-0002 LOCAL ESD | ESD PB | - | - | NORMALLY CLOSE | - | - | L | - | BPCS/SIS | MOT | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G0002 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 5 | - | 1 | - | 660HLS0002 | 660-HLS -0002A | 660-G-0002 STOP | TPL STOP | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G0002 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 6 | - | 1 | - | 660HLS0002A | 660-HLS -0002AA | 660-G-0002 TRIP | CDE TOR | - | - | NORMALLY CLOSE | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G0002 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 7 | - | 1 | - | 660HLS0002R | 660-HLS -0002AR | 660-G-0002 RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G0002 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 8 | - | 1 | - | 660XS0002 | 660-XS -0002A | 660-G-0002 ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G0002 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 9 | - | 1 | - | 660XA0002 | 660-XA -0002A | 660-G-0002 ELEC FAULT | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660G0002 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 10 | - | 1 | - | 660XA0002D | 660-XA -0002AD | 660-G-0002 DISC SECU | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660G0002 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 1 | - | 1 | - | 660HS0003D | 660-HS -0003AD | 660-G-0003 LOCAL START | PB | - | - | NORMALLY OPEN | - | - | L | - | BPCS/SIS | MOT | - | - | - | - | - | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G0003 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 2 | - | 1 | - | 660HSA0003D | 660-HSA -0003AD | 660-G-0003 LOCAL START RECOPIE | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | - | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G0003 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 3 | - | 1 | - | 660HS0003A | 660-HS -0003AA | 660-G-0003 LOCAL ESD | ESD PB | - | - | NORMALLY CLOSE | - | - | L | - | BPCS/SIS | MOT | - | - | - | - | - | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G0003 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 4 | - | 1 | - | 660HSA0003A | 660-HSA -0003AA | 660-G-0003 LOCAL ESD RECOPIE | CONTACT | - | - | NORMALLY CLOSE | - | - | ESS | - | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G0003 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 5 | - | 1 | - | 660HLS0003 | 660-HLS -0003A | 660-G-0003 STOP | TPL STOP | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G0003 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 6 | - | 1 | - | 660HLS0003A | 660-HLS -0003AA | 660-G-0003 TRIP | CDE TOR | - | - | NORMALLY CLOSE | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G0003 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 7 | - | 1 | - | 660HLS0003R | 660-HLS -0003AR | 660-G-0003 RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G0003 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 8 | - | 1 | - | 660XS0003 | 660-XS -0003A | 660-G-0003 ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G0003 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 9 | - | 1 | - | 660XA0003 | 660-XA -0003A | 660-G-0003 ELEC FAULT | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660G0003 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 10 | - | 1 | - | 660XA0003D | 660-XA -0003AD | 660-G-0003 DISC SECU | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660G0003 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 11 | - | 1 | - | 660JT0003 | - | 660-G-0003 | POWER TRANSMITTER | - | - | - | N | - | ESS | ST1C | BPCS/SIS | DCS | - | 0 | 50 | - | Kw | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660G0003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 12 | - | 1 | - | 660JI0003 | - | 660-G-0003 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660G0003 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 1 | - | 1 | - | 660HS0102D | 660-HS -0102AD | 660-G-0102 LOCAL START | PB | - | - | NORMALLY OPEN | - | - | L | - | BPCS/SIS | MOT | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G0102 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 3 | - | 1 | - | 660HS0102A | 660-HS -0102AA | 660-G-0102 LOCAL ESD | ESD PB | - | - | NORMALLY CLOSE | - | - | L | - | BPCS/SIS | MOT | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G0102 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 5 | - | 1 | - | 660HLS0102 | 660-HLS -0102A | 660-G-0102 STOP | TPL STOP | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G0102 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 6 | - | 1 | - | 660HLS0102A | 660-HLS -0102AA | 660-G-0102 TRIP | CDE TOR | - | - | NORMALLY CLOSE | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G0102 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 7 | - | 1 | - | 660HLS0102R | 660-HLS -0102AR | 660-G-0102 RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G0102 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 8 | - | 1 | - | 660XS0102 | 660-XS -0102A | 660-G-0102 ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G0102 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 9 | - | 1 | - | 660XA0102 | 660-XA -0102A | 660-G-0102 ELEC FAULT | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660G0102 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 10 | - | 1 | - | 660XA0102D | 660-XA -0102AD | 660-G-0102 DISC SECU | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660G0102 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 1 | - | 1 | - | 660HS0103D | 660-HS -0103AD | 660-G-0003 LOCAL START | PB | - | - | NORMALLY OPEN | - | - | L | - | BPCS/SIS | MOT | - | - | - | - | - | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G0103 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 2 | - | 1 | - | 660HSA0103D | 660-HSA -0103AD | 660-G-0003 LOCAL START RECOPIE | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | - | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G0103 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 3 | - | 1 | - | 660HS0103A | 660-HS -0103AA | 660-G-0003 LOCAL ESD | ESD PB | - | - | NORMALLY CLOSE | - | - | L | - | BPCS/SIS | MOT | - | - | - | - | - | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G0103 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 4 | - | 1 | - | 660HSA0103A | 660-HSA -0103AA | 660-G-0003 LOCAL ESD RECOPIE | CONTACT | - | - | NORMALLY CLOSE | - | - | ESS | - | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G0103 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 5 | - | 1 | - | 660HLS0103 | 660-HLS -0103A | 660-G-0003 STOP | TPL STOP | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G0103 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 6 | - | 1 | - | 660HLS0103A | 660-HLS -0103AA | 660-G-0003 TRIP | CDE TOR | - | - | NORMALLY CLOSE | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G0103 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 7 | - | 1 | - | 660HLS0103R | 660-HLS -0103AR | 660-G-0003 RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G0103 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 8 | - | 1 | - | 660XS0103 | 660-XS -0103A | 660-G-0003 ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G0103 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 9 | - | 1 | - | 660XA0103 | 660-XA -0103A | 660-G-0003 ELEC FAULT | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660G0103 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 10 | - | 1 | - | 660XA0103D | 660-XA -0103AD | 660-G-0003 DISC SECU | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660G0103 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 11 | - | 1 | - | 660JT0103 | - | 660-G-0103 | POWER TRANSMITTER | - | - | - | N | - | ESS | ST1C | BPCS/SIS | DCS | - | 0 | 50 | - | Kw | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660G0103 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 12 | - | 1 | - | 660JI0103 | - | 660-G-0103 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660G0103 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 1 | - | 1 | - | 660HS5001AD | - | 660-G-5001A LOCAL START | PB | - | - | NORMALLY OPEN | - | - | L | - | BPCS/SIS | MOT | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5001A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 2 | - | 1 | - | 660HSA5001AD | - | 660-G-5001A LOCAL START RECOPIE | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | - | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5001A | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 3 | - | 1 | - | 660HS5001AA | - | 660-G-5001A LOCAL ESD | ESD PB | - | - | NORMALLY CLOSE | - | - | L | - | BPCS/SIS | MOT | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5001A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 4 | - | 1 | - | 660HSA5001AA | - | 660-G-5001A LOCAL ESD RECOPIE | CONTACT | - | - | NORMALLY CLOSE | - | - | ESS | - | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5001A | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 5 | - | 1 | - | 660HLS5001A | - | 660-G-5001A STOP | TPL STOP | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660G5001A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 6 | - | 1 | - | 660HLS5001AA | - | 660-G-5001A TRIP | CDE TOR | - | - | NORMALLY CLOSE | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5001A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 7 | - | 1 | - | 660HLS5001AR | - | 660-G-5001A RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5001A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 8 | - | 1 | - | 660XS5001A | - | 660-G-5001A ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5001A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 9 | - | 1 | - | 660XA5001A | - | 660-G-5001A ELEC FAULT | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660G5001A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 10 | - | 1 | - | 660XA5001AD | - | 660-G-5001A DISC SECU | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660G5001A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 11 | - | 1 | - | 660JT5001A | - | 660-G-5002A | POWER TRANSMITTER | - | - | - | N | - | ESS | ST1C | BPCS/SIS | DCS | - | 0 | 50 | - | Kw | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660G5001A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 12 | - | 1 | - | 660JI5001A | - | 660-G-5002A | INDICATION | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660G5001A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 1 | - | 1 | - | 660HS5001BD | - | 660-G-5001B LOCAL START | PB | - | - | NORMALLY OPEN | - | - | L | - | BPCS/SIS | MOT | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5001B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 2 | - | 1 | - | 660HSA5001BD | - | 660-G-5001B LOCAL START RECOPIE | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | - | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5001B | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 3 | - | 1 | - | 660HS5001BA | - | 660-G-5001B LOCAL ESD | ESD PB | - | - | NORMALLY CLOSE | - | - | L | - | BPCS/SIS | MOT | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5001B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 4 | - | 1 | - | 660HSA5001BA | - | 660-G-5001B LOCAL ESD RECOPIE | CONTACT | - | - | NORMALLY CLOSE | - | - | ESS | - | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5001B | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 5 | - | 1 | - | 660HLS5001B | - | 660-G-5001B STOP | TPL STOP | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660G5001B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 6 | - | 1 | - | 660HLS5001BA | - | 660-G-5001B TRIP | CDE TOR | - | - | NORMALLY CLOSE | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5001B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 7 | - | 1 | - | 660HLS5001BR | - | 660-G-5001B RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5001B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 8 | - | 1 | - | 660XS5001B | - | 660-G-5001B ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5001B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 9 | - | 1 | - | 660XA5001B | - | 660-G-5001B ELEC FAULT | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660G5001B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 10 | - | 1 | - | 660XA5001BD | - | 660-G-5001B DISC SECU | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660G5001B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 11 | - | 1 | - | 660JT5001B | - | 660-G-5002A | POWER TRANSMITTER | - | - | - | N | - | ESS | ST1C | BPCS/SIS | DCS | - | 0 | 50 | - | Kw | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660G5001B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 12 | - | 1 | - | 660JI5001B | - | 660-G-5002A | INDICATION | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660G5001B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 1 | - | 1 | - | 660HS5002AD | - | 660-G-5002A LOCAL START | PB | - | - | NORMALLY OPEN | - | - | L | - | BPCS/SIS | MOT | - | - | - | - | - | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5002A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 2 | - | 1 | - | 660HSA5002AD | - | 660-G-5002A LOCAL START RECOPIE | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5002A | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 3 | - | 1 | - | 660HS5002AA | - | 660-G-5002A LOCAL ESD | ESD PB | - | - | NORMALLY CLOSE | - | - | L | - | BPCS/SIS | MOT | - | - | - | - | - | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5002A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 4 | - | 1 | - | 660HSA5002AA | - | 660-G-5002A LOCAL ESD RECOPIE | CONTACT | - | - | NORMALLY CLOSE | - | - | ESS | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5002A | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 5 | - | 1 | - | 660HLS5002A | - | 660-G-5002A STOP | TPL STOP | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660G5002A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 6 | - | 1 | - | 660HLS5002AA | - | 660-G-5002A TRIP | CDE TOR | - | - | NORMALLY CLOSE | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5002A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 7 | - | 1 | - | 660HLS5002AR | - | 660-G-5002A RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5002A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 8 | - | 1 | - | 660XS5002A | - | 660-G-5002A ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5002A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 9 | - | 1 | - | 660XA5002A | - | 660-G-5002A ELEC FAULT | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660G5002A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 10 | - | 1 | - | 660XA5002AD | - | 660-G-5002A DISC SECU | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660G5002A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 11 | - | 1 | - | 660JI5002A | - | 660-G-5002A | INDICATION | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660G5002A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 12 | - | 1 | - | 660JT5002A | - | 660-G-5002A | POWER TRANSMITTER | - | - | - | N | - | ESS | ST1C | BPCS/SIS | DCS | - | 0 | 50 | - | Kw | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660G5002A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 1 | - | 1 | - | 660HS5002BD | - | 660-G-5002B LOCAL START | PB | - | - | NORMALLY OPEN | - | - | L | - | BPCS/SIS | MOT | - | - | - | - | - | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5002B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 2 | - | 1 | - | 660HSA5002BD | - | 660-G-5002B LOCAL START RECOPIE | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | - | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5002B | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 3 | - | 1 | - | 660HS5002BA | - | 660-G-5002B LOCAL ESD | ESD PB | - | - | NORMALLY CLOSE | - | - | L | - | BPCS/SIS | MOT | - | - | - | - | - | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5002B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 4 | - | 1 | - | 660HSA5002BA | - | 660-G-5002B LOCAL ESD RECOPIE | CONTACT | - | - | NORMALLY CLOSE | - | - | ESS | - | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5002B | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 5 | - | 1 | - | 660HLS5002B | - | 660-G-5002B STOP | TPL STOP | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660G5002B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 6 | - | 1 | - | 660HLS5002BA | - | 660-G-5002B TRIP | CDE TOR | - | - | NORMALLY CLOSE | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5002B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 7 | - | 1 | - | 660HLS5002BR | - | 660-G-5002B RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5002B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 8 | - | 1 | - | 660XS5002B | - | 660-G-5002B ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5002B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 9 | - | 1 | - | 660XA5002B | - | 660-G-5002B ELEC FAULT | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660G5002B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 10 | - | 1 | - | 660XA5002BD | - | 660-G-5002B DISC SECU | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660G5002B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 11 | - | 1 | - | 660JI5002B | - | 660-G-5002A | INDICATION | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660G5002B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 12 | - | 1 | - | 660JT5002B | - | 660-G-5002A | POWER TRANSMITTER | - | - | - | N | - | ESS | ST1C | BPCS/SIS | DCS | - | 0 | 50 | - | Kw | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660G5002B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 1 | - | 1 | - | 660HS5003AD | - | 660-G-5003A LOCAL START | PB | - | - | NORMALLY OPEN | - | - | L | - | BPCS/SIS | MOT | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5003A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 2 | - | 1 | - | 660HSA5003AD | - | 660-G-5003A LOCAL START RECOPIE | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | - | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5003A | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 3 | - | 1 | - | 660HS5003AA | - | 660-G-5003A LOCAL ESD | ESD PB | - | - | NORMALLY CLOSE | - | - | L | - | BPCS/SIS | MOT | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5003A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 4 | - | 1 | - | 660HSA5003AA | - | 660-G-5003A LOCAL ESD RECOPIE | CONTACT | - | - | NORMALLY CLOSE | - | - | ESS | - | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5003A | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 5 | - | 1 | - | 660HLS5003A | - | 660-G-5003A STOP | TPL STOP | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660G5003A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 6 | - | 1 | - | 660HLS5003AA | - | 660-G-5003A TRIP | CDE TOR | - | - | NORMALLY CLOSE | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5003A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 7 | - | 1 | - | 660HLS5003AR | - | 660-G-5003A RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5003A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 8 | - | 1 | - | 660XS5003A | - | 660-G-5003A ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5003A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 9 | - | 1 | - | 660XA5003A | - | 660-G-5003A ELEC FAULT | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660G5003A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 10 | - | 1 | - | 660XA5003AD | - | 660-G-5003A DISC SECU | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660G5003A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 11 | - | 1 | - | 660JI5003A | - | 660-G-5003A | INDICATION | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660G5003A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 12 | - | 1 | - | 660JT5003A | - | 660-G-5003A | POWER TRANSMITTER | - | - | - | N | - | ESS | ST1C | BPCS/SIS | DCS | - | 0 | 50 | - | Kw | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660G5003A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 1 | - | 1 | - | 660HS5003BD | - | 660-G-5003B LOCAL START | PB | - | - | NORMALLY OPEN | - | - | L | - | BPCS/SIS | MOT | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5003B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 2 | - | 1 | - | 660HSA5003BD | - | 660-G-5003B LOCAL START RECOPIE | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | - | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5003B | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 3 | - | 1 | - | 660HS5003BA | - | 660-G-5003B LOCAL ESD | ESD PB | - | - | NORMALLY CLOSE | - | - | L | - | BPCS/SIS | MOT | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5003B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 4 | - | 1 | - | 660HSA5003BA | - | 660-G-5003B LOCAL ESD RECOPIE | CONTACT | - | - | NORMALLY CLOSE | - | - | ESS | - | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5003B | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 5 | - | 1 | - | 660HLS5003B | - | 660-G-5003B STOP | TPL STOP | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660G5003B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 6 | - | 1 | - | 660HLS5003BA | - | 660-G-5003B TRIP | CDE TOR | - | - | NORMALLY CLOSE | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5003B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 7 | - | 1 | - | 660HLS5003BR | - | 660-G-5003B RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5003B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 8 | - | 1 | - | 660XS5003B | - | 660-G-5003B ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5003B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 9 | - | 1 | - | 660XA5003B | - | 660-G-5003B ELEC FAULT | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660G5003B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 10 | - | 1 | - | 660XA5003BD | - | 660-G-5003B DISC SECU | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660G5003B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 11 | - | 1 | - | 660JI5003B | - | 660-G-5003B | INDICATION | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660G5003B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 12 | - | 1 | - | 660JT5003B | - | 660-G-5003B | POWER TRANSMITTER | - | - | - | N | - | ESS | ST1C | BPCS/SIS | DCS | - | 0 | 50 | - | Kw | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660G5003B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 1 | - | 1 | - | 660HS5004AD | - | 660 G 5004A LOCAL START | PB | - | - | NORMALLY OPEN | - | - | L | - | BPCS/SIS | MOT | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5004A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 3 | - | 1 | - | 660HS5004AA | - | 660 G 5004A LOCAL ESD | ESD PB | - | - | NORMALLY CLOSE | - | - | L | - | BPCS/SIS | MOT | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5004A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 4 | - | 1 | - | 660HSA5004AA | - | 660 G 5004A LOCAL ESD RECOPIE | CONTACT | - | - | NORMALLY CLOSE | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5004A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 5 | - | 1 | - | 660HLS5004A | - | 660 G 5004A START/STOP | TPL STOP | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5004A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 6 | - | 1 | - | 660HLS5004AA | - | 660 G 5004A TRIP | CDE TOR | - | - | NORMALLY CLOSE | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5004A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 7 | - | 1 | - | 660HLS5004AR | - | 660 G 5004A RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5004A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 8 | - | 1 | - | 660XS5004A | - | 660 G 5004A ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5004A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 9 | - | 1 | - | 660XA5004A | - | 660 G 5004A ELEC FAULT | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660G5004A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 10 | - | 1 | - | 660XA5004AD | - | 660 G 5004A DISC SECU | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660G5004A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 11 | - | 1 | - | 660HLS5004AM | - | 660 G 5004A START | CDE TOR | - | - | NORMALLY OPEN | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5004A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 1 | - | 1 | - | 660HS5004BD | - | 660 G 5004B LOCAL START | PB | - | - | NORMALLY OPEN | - | - | L | - | BPCS/SIS | MOT | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5004B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 3 | - | 1 | - | 660HS5004BB | - | 660 G 5004B LOCAL ESD | ESD PB | - | - | NORMALLY CLOSE | - | - | L | - | BPCS/SIS | MOT | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5004B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 4 | - | 1 | - | 660HSA5004BB | - | 660 G 5004B LOCAL ESD RECOPIE | CONTACT | - | - | NORMALLY CLOSE | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5004B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 5 | - | 1 | - | 660HLS5004B | - | 660 G 5004B START/STOP | TPL STOP | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5004B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 6 | - | 1 | - | 660HLS5004BA | - | 660 G 5004B TRIP | CDE TOR | - | - | NORMALLY CLOSE | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5004B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 7 | - | 1 | - | 660HLS5004BR | - | 660 G 5004B RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5004B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 8 | - | 1 | - | 660XS5004B | - | 660 G 5004B ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5004B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 9 | - | 1 | - | 660XA5004B | - | 660 G 5004B ELEC FAULT | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660G5004B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 10 | - | 1 | - | 660XA5004BD | - | 660 G 5004B DISC SECU | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660G5004B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 11 | - | 1 | - | 660HLS5004BM | - | 660 G 5004B START | CDE TOR | - | - | NORMALLY OPEN | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5004B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5005D | - | 660 G 5005 LOCAL START | PB | - | - | - | - | - | L | - | BPCS/SIS | MOT | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5005 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660HS5005A | - | 660 G 5005 LOCAL ESD | ESD PB | - | - | - | - | - | L | - | BPCS/SIS | MOT | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5005 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660HLS5005 | - | 660 G 5005 START/STOP | TPL STOP | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5005 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660HLS5005A | - | 660 G 5005 TRIP | CDE TOR | - | - | NORMALLY CLOSE | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5005 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 1 | - | 660HLS5005R | - | 660 G 5005 RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5005 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 1 | - | 660XS5005 | - | 660 G 5005 ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5005 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 9 | - | 1 | - | 660XA5005 | - | 660 G 5005 ELEC FAULT | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660G5005 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 10 | - | 1 | - | 660XA5005D | - | 660 G 5005 DISC SECU | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660G5005 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5007D | - | 660 G 5007 LOCAL START | PB | - | - | - | - | - | L | - | BPCS/SIS | MOT | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5007 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660HS5007A | - | 660 G 5007 LOCAL ESD | ESD PB | - | - | - | - | - | L | - | BPCS/SIS | MOT | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5007 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660HLS5007A | - | 660 G 5007 START/STOP | TPL STOP | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5007 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660HLS5007AA | - | 660 G 5007 TRIP | CDE TOR | - | - | NORMALLY CLOSE | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5007 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 1 | - | 660HLS5007R | - | 660 G 5007 RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5007 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 1 | - | 660XS5007A | - | 660 G 5007 ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5007 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 9 | - | 1 | - | 660XA5007A | - | 660 G 5007 ELEC FAULT | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660G5007 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 10 | - | 1 | - | 660XA5007D | - | 660 G 5007 DISC SECU | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660G5007 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5009D | - | 660 G 5009 LOCAL START | PB | - | - | - | - | - | L | - | BPCS/SIS | MOT | - | - | - | - | - | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5009 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660HS5009A | - | 660 G 5009 LOCAL ESD | ESD PB | - | - | - | - | - | L | - | BPCS/SIS | MOT | - | - | - | - | - | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5009 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660HLS5009 | - | 660 G 5009 START/STOP | TPL STOP | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5009 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660HLS5009A | - | 660 G 5009 TRIP | CDE TOR | - | - | NORMALLY CLOSE | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5009 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 1 | - | 660HLS5009R | - | 660 G 5009 RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5009 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 1 | - | 660XS5009 | - | 660 G 5009 ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5009 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 9 | - | 1 | - | 660XA5009 | - | 660 G 5009 ELEC FAULT | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660G5009 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 10 | - | 1 | - | 660XA5009D | - | 660 G 5009 DISC SECU | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660G5009 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5010D | - | 660 G 5010 LOCAL START | PB | - | - | - | - | - | L | - | BPCS/SIS | MOT | - | - | - | - | - | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5010 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660HS5010A | - | 660 G 5010 LOCAL ESD | ESD PB | - | - | - | - | - | L | - | BPCS/SIS | MOT | - | - | - | - | - | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5010 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660HLS5010 | - | 660 G 5010 START/STOP | TPL STOP | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5010 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660HLS5010A | - | 660 G 5010 TRIP | CDE TOR | - | - | NORMALLY CLOSE | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5010 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 1 | - | 660HLS5010R | - | 660 G 5010 RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5010 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 1 | - | 660XS5010 | - | 660 G 5010 ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660G5010 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 9 | - | 1 | - | 660XA5010 | - | 660 G 5010 ELEC FAULT | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660G5010 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 10 | - | 1 | - | 660XA5010D | - | 660 G 5010 DISC SECU | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660G5010 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS0040 | - | ARRET LOCAL 660E0004A | PB | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660H0040 | U | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660H2_5901 | - | 660-2 GAS DETECTOR (H2) INDICATION | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 5 | 660H25901 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AHH5901_H2 | - | U660H25901 HIGH HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660H25901 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AAX5901_H2 | - | U660H25901 FAULT | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660H25901 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AAH5901_H2 | - | U660H25901 HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660H25901 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660H2_5902 | - | 660-2 GAS DETECTOR (H2) INDICATION | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 5 | 660H25902 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AHH5902_H2 | - | U660H25902 HIGH HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660H25902 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AAX5902_H2 | - | U660H25902 FAULT | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660H25902 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AAH5902_H2 | - | U660H25902 HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660H25902 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5201 | - | JET/DIESEL MODE SELECTOR | HAND SWITCH | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0201 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660H5201 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | CV04 | - | 5 | - | 1 | - | 660LV5191A | - | FROM 660 D 5002 (DIESEL MODE) | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660L5191 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA004 | CI1/CI9 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM536/P08 | - | E10201 | 660IADM512/03 | - | - | - | - | - | - | - | - | 660-3"-P-2041.0-1BB1 | OTHER | L | 6.29 | 8.2 | 40 | 180 | - | - | - | - | III module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-LV -5191A-SP
- | - | - | - | 2 | - | 1 | - | 660HC5220 | - | 660 E 5002 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660H5220 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV12 | - | 7 | - | 1 | - | 660HS5307 | 660-HS -5305 | 660-UVS-5305/5306/5390 | PB | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660H5307 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS506/P02 | - | E10204 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV12 | - | 5 | - | 1 | - | 660HLS5303 | 660-HLS -5301 | 660-UVS-5301 | CONTACT | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660H5303 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV12 | - | 4 | - | 1 | - | 660UZSH5390 | - | 660-UVS-5390 OPEN | LIMIT SWITCH | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5390 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS506/P03 | - | With UZSL | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV12 | - | 8 | - | 1 | - | 660HLS5307 | 660-HLS -5305 | 660-UVS-5305 | CONTACT | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660H5307 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HY5308 | - | AIR/FUEL RATIO | SOFT CALCULATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660H5308 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660HIC5308 | - | AIR/FUEL RATIO | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660H5308 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HV5309 | - | TO 660 E 5010 | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660H5309 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/Pag4 | CI1/CI9 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660HC5309 | - | TO 660 E 5010 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660H5309 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HV5310 | - | TO 660 D 5011 | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660H5310 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/Pag4 | CI1/CI9 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660HC5310 | - | TO 660 D 5011 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660H5310 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HV5311 | - | TO 660 D 5011 | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660H5311 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/Pag4 | CI1/CI9 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660HC5311 | - | TO 660 D 5011 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660H5311 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HV5312 | - | TO 660 D 5011 | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660H5312 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/Pag4 | CI1/CI9 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660HC5312 | - | TO 660 D 5011 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660H5312 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HV5313 | - | TO 660 D 5011 | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660H5313 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/Pag4 | CI1/CI9 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660HC5313 | - | TO 660 D 5011 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660H5313 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5314A | - | EMERGENCY SHUTDOWN | HAND SWITCH | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660H5314 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS504/P01 | - | E10204 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660HS5314B | - | EMERGENCY SHUTDOWN | HAND SWITCH | - | - | - | N | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660H5314 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660HA5314 | 660-XA -5314 | EMERGENCY SHUTDOWN | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660H5314 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5315A | 660-HS -5385A | TOTAL SHUTDOWN | HAND SWITCH | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660H5315 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS504/P02 | - | E10204 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660HS5315B | 660-HS -5385B | TOTAL SHUTDOWN | HAND SWITCH | - | - | - | N | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660H5315 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660HA5315 | 660-HA -5385 | TOTAL SHUTDOWN | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660H5315 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5369A | - | START PILOT A | PB | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660H5369A | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS1-P01 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5369B | - | STOP PILOT A | PB | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660H5369B | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS1-P02 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5371A | - | START PILOT B | PB | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660H5371A | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS1-P03 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5371B | - | STOP PILOT B | PB | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660H5371B | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS1-P04 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5373A | - | START PILOT C | PB | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660H5373A | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS1-P05 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5373B | - | STOP PILOT C | PB | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660H5373B | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS1-P06 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5375A | - | START PILOT D | PB | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660H5375A | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS1-P07 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5375B | - | STOP PILOT D | PB | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660H5375B | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS1-P08 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5383A | - | START BURNER A | PB | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660H5383A | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS1-P09 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5383B | - | STOP BURNER A | PB | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660H5383B | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS1-P10 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5384A | - | START BURNER B | PB | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660H5384A | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS1-P11 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5384B | - | STOP BURNER B | PB | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660H5384B | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS1-P12 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5385A | - | START BURNER C | PB | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660H5385A | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS1-P13 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5385B | - | STOP BURNER C | PB | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660H5385B | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS1-P14 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5386A | - | START BURNER D | PB | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660H5386A | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS1-P15 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5386B | - | STOP BURNER D | PB | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660H5386B | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS1-P16 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5355 | - | ID FAN LOC-O-REM | PB | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660H5355 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS1-P17-P18 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5353 | - | ID FAN STOP | PB | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660H5353 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS1-P19 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5351 | - | ID FAN START | PB | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660H5351 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS1-P20 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5349 | - | FD FAN LOC-O-REM | PB | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660H5349 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS1-P21-P22 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5347 | - | FD FAN STOP | PB | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660H5347 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS1-P23 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5345 | - | FD FAN START | PB | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660H5345 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS1-P24 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5343 | - | EMERGENCY SHUT DOWN | PB | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660H5343 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS1-P25 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5339 | - | HEATER RESET | PB | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660H5339 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS1-P26 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5337 | - | ACK | PB | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660H5337 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS1-P27 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5329 | - | START FUEL GAS TO PILOTS | PB | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660H5329 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS1-P28 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV12 | - | 1 | - | 1 | - | 660HS5380A | - | UVS-5080A | PB | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660H5380 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV12 | - | 2 | - | 1 | - | 660HS5380B | - | UVS-5015 | PB | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660H5380 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5333 | - | STOP FUEL GAS TO PILOTS | PB | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660H5333 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS1-P29 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5331 | - | START FUEL GAS TO BURNERS | PB | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660H5331 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS1-P30 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5335 | - | STOP FUEL GAS TO BURNERS | PB | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660H5335 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS1-P31 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5327 | - | START PURGE | PB | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660H5327 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS1-P32 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5325 | - | START LEAK TEST | PB | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660H5325 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS1-P33 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5358 | - | SPARE | PB | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660H5358 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS1-P34 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5360 | - | SPARE | PB | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660H5360 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS1-P35 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5341 | - | LAMP TEST | PB | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660H5341 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS2-P01 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV13 | - | 4 | - | 1 | - | 660UZSH5006 | - | 660-UV-5006 OPEN | LIMIT SWITCH | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5006 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM500/P01 | - | With UZSL | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV13 | - | 4 | - | 1 | - | 660UZSH5007 | - | 660-UV-5007 OPEN | LIMIT SWITCH | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5007 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM500/P02 | - | With UZSL | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV13 | - | 5 | - | 1 | - | 660UZSL5006 | - | 660-UV-5006 CLOSE | LIMIT SWITCH | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5006 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM500/P03 | - | E10205 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV13 | - | 5 | - | 1 | - | 660UZSL5007 | - | 660-UV-5007 CLOSE | LIMIT SWITCH | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5007 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM500/P04 | - | E10205 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HLS5501 | - | COMRESSOR START/STOP 660 K 5001 | TPL OPEN / CLOSE | - | - | - | N | - | CRD | ST1C | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660H5501 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 4 | - | 1 | - | 660UZSH5014 | - | 660-UVS-5014 OPEN | LIMIT SWITCH | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5014 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS502/P09 | - | With UZSL | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660HS5500 | - | COMRESSOR STOP 660 K 5001 | ESD PB | - | - | - | - | - | CRA | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660H5501 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660XA5500 | - | COMRESSOR PB/ESD 660 K 5001 | ALARM | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660H5501 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HSA5532 | - | ALARM IN COMPRESSOR | ALARM | - | - | - | - | - | LP | ST1D | MAINT | S-PLC | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | FROM ST1 / MMS | - | - | - | 8 | 660H5532 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660LP550/TS1-P01-P02 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5534 | - | HAND SWITCH IN COMPRESSOR | HAND SWITCH | - | - | - | N | - | LP | ST1D | MAINT | S-PLC | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | FROM ST1 / MMS | - | - | - | 7 | 660H5534 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660LP550/TS1-P03 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5536 | - | HAND SWITCH IN COMPRESSOR | HAND SWITCH | - | - | - | N | - | LP | ST1D | MAINT | S-PLC | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | FROM ST1 / MMS | - | - | - | 7 | 660H5536 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660LP550/TS1-P04 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HS5537 | - | HAND SWITCH IN COMPRESSOR | HAND SWITCH | - | - | - | - | - | LP | ST1D | MAINT | S-PLC | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | FROM ST1 / MMS | - | - | - | 7 | 660H5537 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660LP550/TS1-P05 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660HSA_5901 | - | U660HS5901 MANUAL CALL POINT ACTIVATED | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 7 | 660H5901 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660HSA_5902 | - | U660HS5902 MANUAL CALL POINT ACTIVATED | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 7 | 660H5902 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660HSA_5934 | - | PB STOP EMERGENCY | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 7 | 660H5934 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | 660HS_S5934 | - | PB STOP EMERGENCY | PB | - | - | - | - | - | AS | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 7 | 660H5934 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660HSA_5935 | - | PB STOP EMERGENCY | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 7 | 660H5935 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | 660HS_S5935 | - | PB STOP EMERGENCY | PB | - | - | - | - | - | AS | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 7 | 660H5935 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660HSA_5936 | - | PB STOP EMERGENCY | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 7 | 660H5936 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | 660HS_S5936 | - | PB STOP EMERGENCY | PB | - | - | - | N | - | AS | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 7 | 660H5936 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660HSA_5981 | - | U660HS5981 MANUAL CALL POINT ACTIVATED | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 7 | 660H5981 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | 660HS_5981 | - | 660-2 MANUAL CALL POINT(WEATHERPROOF) | PB | - | - | - | N | - | AS | ST1B | SIS | S-PLC-FGS | - | 0 | 100 | - | %LEL | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 7 | 660H5981 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJGS592/ P08 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | U660AAH1901_HC | - | U660HC1901 HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC1901 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | U660AAX1901_HC | - | U660HC1901 FAULT | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC1901 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | U660AHH1901_HC | - | U660HC1901 HIGH HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC1901 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | U660HC_1901 | - | 660-1 GAS DETECTOR(HC) INDICATION | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 5 | 660HC1901 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | U660HC_S_5500 | - | 660-2 GAS DETECTOR SAFETY(HC) IN 660K5001 | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 5 | 660HC5500 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | U660AAX5500_HC | - | 660-2 GAS DETECTOR SAFETY(HC) IN 660K5001 | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5500 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | U660ASH5500_HC | - | 660-2 GAS DETECTOR SAFETY(HC) IN 660K5001 | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1B | SIS | S-PLC-FGS | - | - | - | 20% | - | P22201-100-03 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5500 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | U660ASHH5500_HC | - | 660-2 GAS DETECTOR SAFETY(HC) IN 660K5001 | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1B | SIS | S-PLC-FGS | - | - | - | 40% | - | P22201-100-03 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5500 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660HC_5901 | - | 660-2 GAS DETECTOR(HC) INDICATION | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 5 | 660HC5901 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AHH5901_HC | - | U660HC5901 HIGH HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5901 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AAX5901_HC | - | U660HC5901 FAULT | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5901 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AAH5901_HC | - | U660HC5901 HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5901 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660HC_5902 | - | 660-2 GAS DETECTOR(HC) INDICATION | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 5 | 660HC5902 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AHH5902_HC | - | U660HC5902 HIGH HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5902 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AAX5902_HC | - | U660HC5902 FAULT | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5902 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AAH5902_HC | - | U660HC5902 HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5902 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660HC_5903 | - | 660-2 GAS DETECTOR(HC) INDICATION | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 5 | 660HC5903 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AHH5903_HC | - | U660HC5903 HIGH HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5903 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AAX5903_HC | - | U660HC5903 FAULT | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5903 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AAH5903_HC | - | U660HC5903 HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5903 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660HC_5904 | - | 660-2 GAS DETECTOR(HC) INDICATION | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 5 | 660HC5904 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AHH5904_HC | - | U660HC5904 HIGH HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5904 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AAX5904_HC | - | U660HC5904 FAULT | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5904 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AAH5904_HC | - | U660HC5904 HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5904 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 2 | - | U660HC_5905 | - | 660-2 GAS DETECTOR(HC) INDICATION | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 5 | 660HC5905 | C2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 2 | - | U660AHH5905_HC | - | U660HC5905 HIGH HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5905 | C2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 2 | - | U660AAX5905_HC | - | U660HC5905 FAULT | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5905 | C2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 2 | - | U660AAH5905_HC | - | U660HC5905 HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5905 | C2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AAX5906_HC | - | U660HC5906 FAULT | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5906 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AHH5906_HC | - | U660HC5906 HIGH HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5906 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660HC_5906 | - | 660-2 GAS DETECTOR(HC) INDICATION | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 5 | 660HC5906 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AAH5906_HC | - | U660HC5906 HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5906 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660HC_5907 | - | 660-2 GAS DETECTOR(HC) INDICATION | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 5 | 660HC5907 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AHH5907_HC | - | U660HC5907 HIGH HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5907 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AAX5907_HC | - | U660HC5907 FAULT | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5907 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AAH5907_HC | - | U660HC5907 HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5907 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 2 | - | U660HC_5908 | - | 660-2 GAS DETECTOR(HC) INDICATION | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 5 | 660HC5908 | C2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 2 | - | U660AHH5908_HC | - | U660HC5908 HIGH HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5908 | C2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 2 | - | U660AAX5908_HC | - | U660HC5908 FAULT | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5908 | C2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 2 | - | U660AAH5908_HC | - | U660HC5908 HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5908 | C2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660HC_5909 | - | 660-2 GAS DETECTOR(HC) INDICATION | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 5 | 660HC5909 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AHH5909_HC | - | U660HC5909 HIGH HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5909 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AAH5909_HC | - | U660HC5909 HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5909 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AAX5909_HC | - | U660HC5909 FAULT | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5909 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660HC_5910 | - | 660-2 GAS DETECTOR(HC) INDICATION | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 5 | 660HC5910 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AHH5910_HC | - | U660HC5910 HIGH HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5910 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AAX5910_HC | - | U660HC5910 FAULT | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5910 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AAH5910_HC | - | U660HC5910 HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5910 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660HC_5911 | - | 660-2 GAS DETECTOR(HC) INDICATION | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 5 | 660HC5911 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AHH5911_HC | - | U660HC5911 HIGH HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5911 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AAX5911_HC | - | U660HC5911 FAULT | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5911 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AAH5911_HC | - | U660HC5911 HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5911 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660HC_5912 | - | 660-2 GAS DETECTOR(HC) INDICATION | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 5 | 660HC5912 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AHH5912_HC | - | U660HC5912 HIGH HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5912 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AAX5912_HC | - | U660HC5912 FAULT | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5912 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AAH5912_HC | - | U660HC5912 HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5912 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660HC_5913 | - | 660-2 GAS DETECTOR(HC) INDICATION | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 5 | 660HC5913 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AHH5913_HC | - | U660HC5913 HIGH HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5913 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AAX5913_HC | - | U660HC5913 FAULT | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5913 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AAH5913_HC | - | U660HC5913 HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5913 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660HC_S_5931 | - | LEL DETECTOR C3H8 | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 5 | 660HC5931 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | 660HC_S_5931 | - | LEL DETECTOR C3H8 | GAS DETECTOR HC | - | - | 3 WIRES | N | - | AS | ST1B | SIS | S-PLC-FGS | - | 0 | 100 | - | %LEL | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 3 | 660HC5931 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI50 | INT | - | - | - | - | - | - | - | - | - | - | 660BJGS591/ T02 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660ASHH5931_HC | - | LEL DETECTOR C3H8 | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1B | SIS | S-PLC-FGS | - | - | - | 40% | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5931 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660ASH5931_HC | - | LEL DETECTOR C3H8 | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1B | SIS | S-PLC-FGS | - | - | - | 20% | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5931 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AAX5931_HC | - | LEL DETECTOR C3H8 | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5931 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660HC_S_5932 | - | LEL DETECTOR C3H8 | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 5 | 660HC5932 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | 660HC_S_5932 | - | LEL DETECTOR C3H8 | GAS DETECTOR HC | - | - | 3 WIRES | N | - | AS | ST1B | SIS | S-PLC-FGS | - | 0 | 100 | - | %LEL | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 3 | 660HC5932 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI50 | INT | - | - | - | - | - | - | - | - | - | - | 660BJGS591/ T03 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660ASHH5932_HC | - | LEL DETECTOR C3H8 | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1B | SIS | S-PLC-FGS | - | - | - | 40% | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5932 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660ASH5932_HC | - | LEL DETECTOR C3H8 | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1B | SIS | S-PLC-FGS | - | - | - | 20% | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5932 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AAX5932_HC | - | LEL DETECTOR C3H8 | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5932 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660HC_S_5981 | - | 660-2 GAS DETECTOR SAFETY(HC) INDICATION | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 5 | 660HC5981 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | 660HC_S_5981 | - | 660-2 GAS DETECTOR SAFETY(HC) | GAS DETECTOR HC | - | - | 3 WIRES | N | - | AS | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 3 | 660HC5981 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI50 | INT | - | - | - | - | - | - | - | - | - | - | 660BJGS591/ T01 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660ASHH5981_HC | - | U660HC5981 HIGH HIGH | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1B | SIS | S-PLC-FGS | - | - | - | 40% | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5981 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660ASH5981_HC | - | U660HC5981 HIGH HIGH | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1B | SIS | S-PLC-FGS | - | - | - | 20% | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5981 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AAX5981_HC | - | U660HC5981 FAULT | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5981 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660HC_S_5982 | - | 660-2 GAS DETECTOR SAFETY(HC) INDICATION | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 5 | 660HC5982 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | 660HC_S_5982 | - | 660-2 GAS DETECTOR SAFETY(HC) | GAS DETECTOR HC | - | - | 3 WIRES | N | - | AS | ST1B | SIS | S-PLC-FGS | - | 0 | 100 | - | %LEL | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 3 | 660HC5982 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI50 | INT | - | - | - | - | - | - | - | - | - | - | 660BJGS591/ T04 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660ASHH5982_HC | - | U660HC5982 HIGH HIGH | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1B | SIS | S-PLC-FGS | - | - | - | 40% | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 7 | 660HC5982 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660ASH5982_HC | - | U660HC5982 HIGH HIGH | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1B | SIS | S-PLC-FGS | - | - | - | 20% | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 7 | 660HC5982 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | U660AAX5982_HC | - | U660HC5982 FAULT | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660HC5982 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 1 | - | 1 | - | 660HSK5001D | - | 660 KM 5001 LOCAL START | PB | - | - | - | - | - | L | - | SIS | MOT | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660K5001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 3 | - | 1 | - | 660HSK5001A | - | 660 KM 5001 LOCAL ESD | ESD PB | - | - | - | - | - | L | - | SIS | MOT | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660K5001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 4 | - | 1 | - | 660HSAK5001A | - | 660 KM 5001 LOCAL ESD RECOPIE | CONTACT | - | - | - | N | - | ESS | ST1 | SIS | S-PLC | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660K5001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 5 | - | 1 | - | 660HLSK5001 | - | 660 KM 5001 START/STOP | TPL STOP | - | - | - | - | - | CRD | SdC | SIS | DCS | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660K5001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 6 | - | 1 | - | 660HLSK5001A | - | 660 KM 5001 TRIP | CDE TOR | - | - | - | N | - | ESS | ST1 | SIS | S-PLC | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660K5001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 7 | - | 1 | - | 660HLSK5001R | - | 660 KM 5001 RUNNING STATUS | CONTACT | - | - | - | N | - | ESS | ST1 | SIS | S-PLC | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660K5001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 8 | - | 1 | - | 660XSK5001 | - | 660 KM 5001 ELEC FAULT | CONTACT | - | - | - | N | - | ESS | ST1 | SIS | S-PLC | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660K5001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 9 | - | 1 | - | 660XAK5001 | - | 660 KM 5001 ELEC FAULT | ALARM | - | - | - | N | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660K5001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 10 | - | 1 | - | 660XAK5001D | - | 660 KM 5001 DISC SECU | ALARM | - | - | - | - | - | CRD | SdC | SIS | DCS | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660K5001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 11 | - | 1 | - | 660HLSK5001M | - | 660 KM 5001 START | CDE TOR | - | - | - | N | - | ESS | ST1 | SIS | S-PLC | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660K5001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 1 | - | 1 | - | 660HSK5002D | - | 660 KM 5002 LOCAL START | PB | - | - | - | - | - | L | - | SIS | MOT | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660K5002 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 3 | - | 1 | - | 660HSK5002A | - | 660 KM 5002 LOCAL ESD | ESD PB | - | - | - | - | - | L | - | SIS | MOT | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660K5002 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 4 | - | 1 | - | 660HSAK5002A | - | 660 KM 5002 LOCAL ESD RECOPIE | CONTACT | - | - | - | N | - | ESS | ST1 | SIS | S-PLC | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660K5002 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 5 | - | 1 | - | 660HLSK5002 | - | 660 KM 5002 START/STOP | TPL STOP | - | - | - | - | - | CRD | SdC | SIS | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660K5002 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 6 | - | 1 | - | 660HLSK5002A | - | 660 KM 5002 TRIP | CDE TOR | - | - | - | N | - | ESS | ST1 | SIS | S-PLC | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660K5002 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 7 | - | 1 | - | 660HLSK5002R | - | 660 KM 5002 RUNNING STATUS | CONTACT | - | - | - | N | - | ESS | ST1 | SIS | S-PLC | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660K5002 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 8 | - | 1 | - | 660XSK5002 | - | 660 KM 5002 ELEC FAULT | CONTACT | - | - | - | N | - | ESS | ST1 | SIS | S-PLC | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660K5002 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 9 | - | 1 | - | 660XAK5002 | - | 660 KM 5002 ELEC FAULT | ALARM | - | - | - | N | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660K5002 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 10 | - | 1 | - | 660XAK5002D | - | 660 KM 5002 DISC SECU | ALARM | - | - | - | - | - | CRD | SdC | SIS | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660K5002 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 11 | - | 1 | - | 660HLSK5002M | - | 660 KM 5002 START | CDE TOR | - | - | - | N | - | ESS | ST1 | SIS | S-PLC | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660K5002 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC11 | - | 1 | - | 1 | - | 660HSK5003D | 660-HS -5003KD | 660K5003 LOCAL START | PB | - | - | NORMALLY OPEN | - | - | L | - | BPCS/SIS | VSD | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660K5003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC11 | - | 2 | - | 1 | - | 660HSK5003A | 660-HS -5003KA | 660K5003 LOCAL ESD | PB | - | - | NORMALLY CLOSE | - | - | L | - | BPCS/SIS | VSD | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660K5003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC11 | - | 3 | - | 1 | - | 660HLSK5003 | 660-HLS -5003K | 660K5003 STOP | TPL STOP | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660K5003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC11 | - | 4 | - | 1 | - | 660HLSK5003A | 660-HLS -5003KA | 660K5003 TRIP | CDE TOR | - | - | NORMALLY CLOSE | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660K5003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC11 | - | 5 | - | 1 | - | 660HLSK5003R | 660-HLS -5003KR | 660K5003 RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660K5003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC11 | - | 6 | - | 1 | - | 660XSK5003 | 660-XS -5003K | 660K5003 ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660K5003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC11 | - | 7 | - | 1 | - | 660XAK5003 | 660-XA -5003K | 660K5003 ELEC FAULT | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660K5003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC11 | - | 8 | - | 1 | - | 660XAK5003D | 660-XA -5003KD | 660K5003 DISC SECU | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660K5003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC11 | - | 9 | - | 1 | - | 660SIK5003 | 660-SI -5003K | 660K5003 SPEED | SPEED | - | - | - | N | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660K5003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC11 | - | 10 | - | 1 | - | 660SCK5003 | 660-SC -5003K | 660K5003 SPEED SET POINT | OPER SETPOINT | - | - | - | N | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660K5003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO12 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC11 | - | 13 | - | 1 | - | 660XSK5003F | 660-XS -5003KF | 660K5003 VSD FAULT | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660K5003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC11 | - | 14 | - | 1 | - | 660XAK5003F | 660-XA -5003KF | 660K5003 VSD FAULT | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660K5003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC11 | - | 1 | - | 1 | - | 660HSK5004D | 660-HS -5004KD | 660K5004 LOCAL START | PB | - | - | NORMALLY OPEN | - | - | L | - | BPCS/SIS | VSD | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660K5004 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC11 | - | 2 | - | 1 | - | 660HSK5004A | 660-HS -5004KA | 660K5004 LOCAL ESD | PB | - | - | NORMALLY CLOSE | - | - | L | - | BPCS/SIS | VSD | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660K5004 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC11 | - | 3 | - | 1 | - | 660HLSK5004 | 660-HLS -5004K | 660K5004 STOP | TPL STOP | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660K5004 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC11 | - | 4 | - | 1 | - | 660HLSK5004A | 660-HLS -5004KA | 660K5004 TRIP | CDE TOR | - | - | NORMALLY CLOSE | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660K5004 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC11 | - | 5 | - | 1 | - | 660HLSK5004R | 660-HLS -5004KR | 660K5004 RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1 | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660K5004 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC11 | - | 6 | - | 1 | - | 660XSK5004 | 660-XS -5004K | 660K5004 ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660K5004 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC11 | - | 7 | - | 1 | - | 660XAK5004 | 660-XA -5004K | 660K5004 ELEC FAULT | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660K5004 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC11 | - | 8 | - | 1 | - | 660XAK5004D | 660-XA -5004KD | 660K5004 DISC SECU | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660K5004 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC11 | - | 9 | - | 1 | - | 660SIK5004 | 660-SI -5004K | 660K5004 SPEED | SPEED | - | - | - | N | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660K5004 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC11 | - | 10 | - | 1 | - | 660SCK5004 | 660-SC -5004K | 660K5004 SPEED SET POINT | OPER SETPOINT | - | - | - | N | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660K5004 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO12 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC11 | - | 13 | - | 1 | - | 660XSK5004F | 660-XS -5004KF | 660K5004 VSD FAULT | CONTACT | - | - | NORMALLY OPEN | N | - | ESS | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660K5004 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC11 | - | 14 | - | 1 | - | 660XAK5004F | 660-XA -5004KF | 660K5004 VSD FAULT | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660K5004 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660LG0003A | - | DEBUTANIZER | LEVEL GLASS | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660L0003A | U | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660LG0003B | - | DEBUTANIZER | LEVEL GLASS | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660L0003B | U | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660LT0008 | - | LT0009 INTERFACE D0004 | PRESSURE DP | - | - | W/T SEAL+CAPILLARY | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660L0008 | D1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660LDT0009 | - | LDT0009 INTERFACE D0004 | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660L0009 | D1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660LAH0010 | - | LAH0010 ESSENCE D0004 | LEVEL SWITCH | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L0010 | D1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660LSL0010 | - | LSL0010 EIPS D0004 ARRET G0003-0103 | LEVEL SWITCH | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660L0010 | D1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660LDAL0011 | - | LDAL0011 INTERFACE D0004 | LEVEL SWITCH | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L0011 | D1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 2 | - | 660LAH0041 | - | DEBUTANIZER | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | 1790 | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L0041 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 2 | - | 660LAL0041 | - | DEBUTANIZER | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | 1045 | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L0041 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 2 | - | 660LAX0041 | - | DEBUTANIZER | SOFT CALCULATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L0041 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | CV01 | - | 1 | - | 1 | - | 660LV5005 | - | NAPHTHA OFF-SPEC TO 660 E 0002A/B | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660L5005 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA004 | CI1/CI9 | NO | - | PP | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2042.0-1BB1 | - | - | - | - | - | - | - | - | - | - | III module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660LC5005 | 660-LY -5005 | NAPHTHA OFF-SPEC TO 660-E-0002A/B | LEVEL CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660L5005 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660HS5005 | - | NAPHTHA OFF-SPEC TO 660-E-0002A/B | HAND SWITCH | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660L5005 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660LTS5006 | - | DEBUTANIZER RECEIVER | PRESSURE DP | - | - | W/T SEAL+CAPILLARY | N | - | L | ST1D | BPCS/SIS | S-PLC | - | 0 | 100 | - | % | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660L5006 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-430 / PART 1 FOLIO 2 | CI6 | NO | - | NI (NOT INSULATED) | - | - | -749 | mmH2O 4°C | - | -364.38 | mmH2O 4°C | - | -10000 | mmH2O 4°C | - | 10000 | mmH2O 4°C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS534/P02 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | OTHER | OTHER | 3.8 | 5.5 | 40 | 120 | - | - | - | - | PED Group: 1 Phase Gas | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-LTS -5006-SP
- | - | - | - | 2 | - | 1 | - | 660LI5006 | - | 660D0004 - 660LTS5006 | LEVEL INDICATOR | - | - | - | N | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660L5006 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -2500 | mbar | - | 2500 | mbar | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660LAH5006 | 660-LSH -5006 | 660D0004 - 660LTS5006 | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | Note3 | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L5006 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660LSLL5006 | - | 660D0004 - 660LTS5006 | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | Note3 | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660L5006 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-LSLL -5006-SP
- | - | - | - | 5 | - | 1 | - | 660LAX5006 | - | 660D0004 - 660LTS5006 | SOFT CALCULATION | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - |  | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L5006 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660LG5007 | - | DEBUTANIZER RECEIVER | MAGNETIC GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660L5007 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | GS-RC-INS-200 / APPENDIX 14-T3 | CΙ2 / CΙ6 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | OTHER | OTHER | 3.8 | 5.5 | 40 | 120 | - | - | - | - | Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-LG -5007-SP
- | - | - | - | 1 | - | 1 | - | 660LT5008 | - | DEBUTANIZER RECEIVER | PRESSURE DP | - | - | W/T SEAL+CAPILLARY | - | - | L | ST1C | BPCS | DCS | - | 0 | 100 | - | % | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660L5008 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-430 / PART 1 FOLIO 2 | CI6 | NO | - | NI (NOT INSULATED) | - | - | -749 | mmH2O 4°C | - | -364.38 | mmH2O 4°C | - | -10000 | mmH2O 4°C | - | 10000 | mmH2O 4°C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM535/P05 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | OTHER | OTHER | 3.8 | 5.5 | 40 | 120 | - | - | - | - | PED Group: 1 Phase Gas | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-LT -5008-SP
- | - | - | - | 2 | - | 1 | - | 660LC5008 | - | 660D0004 - 660LTS5008 | LEVEL CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660L5008 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -2500 | mbar | - | 2500 | mbar | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660LAL5008 | - | 660D0004 - 660LTS5008 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | Note3 | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L5008 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -2500 | mbar | - | 2500 | mbar | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660LG5091 | 660LG5091R | PRODUCT FRACTIONATOR KEROSENE DRAW TRAY | MAGNETIC GAUGE | - | - | - | N | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660L5091 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | GS-RC-INS-200 / APPENDIX 14-T3 | CΙ2 / CΙ6 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | OTHER | OTHER | 0.8 | 4 | 213 | 390 | - | - | - | - | Group:1 Phase: Gas | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-LG -5091-SP
- | - | - | - | 1 | - | 1 | - | 660LG5092 | - | PRODUCT FRACTIONATOR BOTTOM | MAGNETIC GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660L5092 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | GS-RC-INS-200 / APPENDIX 14-T3 | CΙ2 / CΙ6 | P | LP | TV2 | STD RC INS 220 / FOLIO 44 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | OTHER | OTHER | 1.5 | 4.2 | 356 | 390 | - | - | - | - | Group: 1 Phase: Gas | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-LG -5092-SP
- | - | - | - | 1 | - | 1 | - | 660LG5093A | - | 660-C-5002 | MAGNETIC GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660L5093 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | GS-RC-INS-200 / APPENDIX 14-T3 | CΙ2 / CΙ6 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | OTHER | OTHER | 1.1 | 4.1 | 247 | 310 | - | - | - | - | Group: 1 Phase: Gas | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-LG -5093A-SP
- | - | - | - | 2 | - | 1 | - | 660LG5093B | - | 660-C-5002 | MAGNETIC GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660L5093 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | GS-RC-INS-200 / APPENDIX 14-T3 | CΙ2 / CΙ6 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | OTHER | OTHER | 1.1 | 4.1 | 247 | 310 | - | - | - | - | Group: 1 Phase: Gas | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-LG -5093B-SP
- | - | - | - | 1 | - | 1 | - | 660LAH5095 | - | 660-C-5001 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L5095 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660LAL5095 | - | 660-C-5001 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L5095 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660LI5095 | - | 660C5001 - 660LT5095 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660L5095 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660LT5096 | - | PRODUCT FRACTIONATOR BOTTOM | GUIDED WAVE RADAR | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 100 | - | % | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660L5096 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | GS-RC-INS-200 / APPENDIX 14_T4 | CΙ2 / CΙ6 (TBC) | P | LP | TV2 | STD RC INS 220 / FOLIO 45 | - | 0 | mm | - | 1950 | mm | - | 0 | mm | - | 1950 | mm | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM531/P13 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | OTHER | OTHER | 1.5 | 4.2 | 356 | 390 | - | - | - | - | - | - | - | - | - | ATEX | 2 | II | - | - | - | - | - | - | - | - | 660-LT -5096-SP
- | - | - | - | 1 | - | 1 | - | 660LAH5096 | - | 660C5001 - 660LT5096 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | Note1 | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L5096 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660LAL5096 | - | 660C5001 - 660LT5096 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | Note1 | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L5096 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660LC5096 | - | 660C5001 - 660LT5096 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660L5096 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | CV01 | - | 5 | - | 1 | - | 660LV5097 | - | 660 C 5002 | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660L5097 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA004 | CI1/CI9 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM531/P14 | - | E10201 | 660IADM513/05 | - | - | - | - | - | - | - | - | 660-6"-P-2003.0-1BB1 | OTHER | L | 3.23 | 6 | 167 | 310 | - | - | - | - | III module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-LV -5097-SP
- | - | - | - | 1 | - | 1 | - | 660LAH5097 | - | 660-C-5002 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | Note2 | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L5097 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660LAL5097 | - | 660C5002 - 660FT5097 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | Note2 | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L5097 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660LC5097 | - | 660C5002 - 660FT5097 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660L5097 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660PDT5085 | - | KEROSENE STRIPPER REBOILER BYPASS | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 4 | - | bar | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5085 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-411 / PART 2 FOLIO 3 | CI2 | P | LP | TV2 | STD RC INS 220 / FOLIO 26 | - | 0 | bar | - | 4 | bar | - | -5000 | mbar | - | 5000 | mbar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM530/P12 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-6"-P-2076.0-3BB3 | OTHER | L | 13.5 | 19 | 357 | 390 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PDT -5085-SP
- | - | - | - | 2 | - | 1 | - | 660PT5083 | - | KEROSENE STRIPPER OVERHEAD | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -0.5 | 2 | - | bar Gage | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5083 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 11 | CI6 | NO | - | CC | - | - | -0.5 | bar | Gage | 2 | bar | Gage | -1 | bar | Gage | 35 | bar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM531/P15 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-8"-P-2011.0-1BB1 | KERO | OTHER | 0.84 | 4 | 216 | 310 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PT -5083-SP
- | - | - | - | 1 | - | 1 | - | 660LY5153 | - | TO 660D5001 | SOFT CALCULATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660L5153 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660LAH5191 | - | 660-D-5002 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | Note:5 | - | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L5191 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660LAL5191 | - | 660D5002 - 660LT5191 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | Note:5 | - | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L5191 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660LC5191 | - | 660D5002 - 660LT5191 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660L5191 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | CV04 | - | 6 | - | 1 | - | 660LV5191B | - | 660 D 5002 (JET MODE) | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660L5191 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA004 | CI1/CI9 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM536/P09 | - | E10201 | 660IADM512/04 | - | - | - | - | - | - | - | - | 660-3"-P-2041.1-1BB1 | OTHER | L | 6.29 | 8.2 | 40 | 180 | - | - | - | - | III module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-LV -5191B-SP
- | - | - | - | 2 | - | 1 | - | 660PT5180 | - | PRODUCT FRACTIONATOR CONDENDER INLET | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -0.5 | 2 | - | bar Gage | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5180 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 11 | CI6 | NO | - | PP | - | - | -0.5 | bar | Gage | 2 | bar | Gage | -1 | bar | Gage | 35 | bar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM536/P10 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-24"-P-2002.0-1BB1 | OTHER | OTHER | 0.78 | 3.5 | 109 | 145 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PT -5180-SP
- | - | - | - | 2 | - | 1 | - | 660PT5234 | - | LP STEAM FROM OSBL | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 10 | - | bar Gage | 214359C-6602-PID-0041-0002 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5234 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 3 | CI2 | NO | - | CC | - | - | 0 | bar | Gage | 10 | bar | Gage | -1 | bar | Gage | 35 | bar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM536/P11 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-6"-VB-2066.0-1BS1 | STEAM LP | OTHER | 4.5 | 5.5 | 170 | 200 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PT -5234-SP
- | - | - | - | 7 | - | 1 | - | 660LY5191 | - | 660D5002 - 660LT5191 | SOFT CALCULATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660L5191 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/Pag4 | CI1/CI9 | NO | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660LG5192 | 660LG5192R | 660-D-5002 | MAGNETIC GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660L5192 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | GS-RC-INS-200 / APPENDIX 14-T3 | CΙ2 / CΙ6 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | OTHER | OTHER | 6.3 | 8 | 40 | 180 | - | - | - | - | Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-LG -5192-SP
- | - | - | - | 2 | - | 1 | - | 660FTS5270A | - | TO 660 F 5001 | PRESSURE DP | - | - | - | - | - | L | ST1D | BPCS/SIS | CONV | - | 0 | 265 | - | m³/h | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5270 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-420 / PART 2 FOLIO 6 | CΙ6 | P | LP | TV2 | STD RC INS 220 / FOLIO 30 | - | 0 | mbar | - | 250 | mbar | - | -1000 | mbar | - | 1000 | mbar | - | - | - | - | - | - | - | - | NR | - | 660FTS5270A | - | - | - | - | - | - | - | 660BJMS531/P03 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-8"-P-2009.3-3BB3 | OTHER | L | 8.77 | 19 | 357 | 390 | - | - | - | - | PED Fluid Group: 1. Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FTS -5270A-SP
- | - | - | - | 3 | - | 1 | - | 660FTS5270B | - | TO 660 F 5001 | PRESSURE DP | - | - | - | - | - | L | ST1D | BPCS/SIS | CONV | - | 0 | 265 | - | m³/h | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5270 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-420 / PART 2 FOLIO 6 | CΙ6 | P | LP | TV2 | STD RC INS 220 / FOLIO 30 | - | 0 | mbar | - | 250 | mbar | - | -1000 | mbar | - | 1000 | mbar | - | - | - | - | - | - | - | - | NR | - | 660FTS5270B | - | - | - | - | - | - | - | 660BJMS531/P04 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-8"-P-2009.3-3BB3 | OTHER | L | 8.77 | 19 | 357 | 390 | - | - | - | - | PED Fluid Group: 1. Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FTS -5270B-SP
- | - | - | - | 4 | - | 1 | - | 660FTS5270C | - | TO 660 F 5001 | PRESSURE DP | - | - | - | - | - | L | ST1D | BPCS/SIS | CONV | - | 0 | 265 | - | m³/h | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5270 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-420 / PART 2 FOLIO 6 | CΙ6 | P | LP | TV2 | STD RC INS 220 / FOLIO 30 | - | 0 | mbar | - | 250 | mbar | - | -1000 | mbar | - | 1000 | mbar | - | - | - | - | - | - | - | - | NR | - | 660FTS5270C | - | - | - | - | - | - | - | 660BJMS540/P02 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-8"-P-2009.3-3BB3 | OTHER | L | 8.77 | 19 | 357 | 390 | - | - | - | - | PED Fluid Group: 1. Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FTS -5270C-SP
- | - | - | - | 4 | - | 1 | - | 660LTS5193AA | - | 660D5001 - 660LTS5193ABC | OUTPUT CONVERTER | - | - | - | N | - | ITR | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660L5193 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660LTS5193BA | - | 660D5001 - 660LTS5193ABC | OUTPUT CONVERTER | - | - | - | N | - | ITR | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660L5193 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660LTS5193CA | - | 660D5001 - 660LTS5193ABC | OUTPUT CONVERTER | - | - | - | N | - | ITR | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660L5193 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 1 | - | 660LTS5193AB | - | LEVEL ON 660D5001 - 660LTS5193ABC | OUTPUT CONVERTER | - | - | - | N | - | ITR | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660L5193 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | EXT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 1 | - | 660LTS5193BB | - | LEVEL ON 660D5001 - 660LTS5193ABC | OUTPUT CONVERTER | - | - | - | N | - | ITR | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660L5193 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | EXT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 9 | - | 1 | - | 660LTS5193CB | - | LEVEL ON 660D5001 - 660LTS5193ABC | OUTPUT CONVERTER | - | - | - | N | - | ITR | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660L5193 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | EXT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 10 | - | 1 | - | 660LI5193A | - | 660D5001 - 660LTS5193ABC | INDICATION | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660L5193 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 11 | - | 1 | - | 660LI5193B | - | 660D5001 - 660LTS5193ABC | INDICATION | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660L5193 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 12 | - | 1 | - | 660LI5193C | - | 660D5001 - 660LTS5193ABC | INDICATION | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660L5193 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 13 | - | 1 | - | 660LSHH5193AA | - | 660D5001 - 660LTS5193ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1D | BPCS/SIS | S-PLC | - | - | - | Note:4 | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660L5193 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 14 | - | 1 | - | 660LSHH5193BA | - | 660D5001 - 660LTS5193ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1D | BPCS/SIS | S-PLC | - | - | - | Note:4 | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660L5193 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 15 | - | 1 | - | 660LSHH5193CA | - | 660D5001 - 660LTS5193ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1D | BPCS/SIS | S-PLC | - | - | - | Note:4 | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660L5193 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 16 | - | 1 | - | 660LSLL5193AA | - | 660D5001 - 660LTS5193ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1D | BPCS/SIS | S-PLC | - | - | - | Note:4 | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660L5193 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 17 | - | 1 | - | 660LSLL5193BA | - | 660D5001 - 660LTS5193ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1D | BPCS/SIS | S-PLC | - | - | - | Note:4 | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660L5193 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 18 | - | 1 | - | 660LSLL5193CA | - | 660D5001 - 660LTS5193ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1D | BPCS/SIS | S-PLC | - | - | - | Note:4 | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660L5193 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 19 | - | 1 | - | 660LAHH5193 | - | 660D5001 - 660LTS5193ABC | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | Note:4 | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L5193 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 20 | - | 1 | - | 660LALL5193 | - | 660D5001 - 660LTS5193ABC | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | Note:4 | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L5193 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 21 | - | 1 | - | 660LAX5193 | - | 660D5001 - 660LTS5193ABC | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L5193 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 22 | - | 1 | - | 660LSH5193 | - | 660D5001 - 660LTS5193ABC | ALARM | - | - | - | N | - | ITR | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660L5193 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 23 | - | 1 | - | 660LSL5193 | - | 660D5001 - 660LTS5193ABC | ALARM | - | - | - | N | - | ITR | ST1C | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660L5193 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 24 | - | 1 | - | 660LAH5193 | - | 660D5001 - 660LTS5193ABC | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | Note:4 | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L5193 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 25 | - | 1 | - | 660LAL5193 | - | 660D5001 - 660LTS5193ABC | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | Note:4 | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L5193 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 26 | - | 1 | - | 660LC5193 | 660-LC -5194 | 660D5001 - 660LTS5193ABC | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660L5193 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 27 | - | 1 | - | 660LC5193AB | - | 660-D-5001 | CONTROLLER | - | - | - | - | - | - | - | BPCS/SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660L5193 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 28 | - | 1 | - | 660LC5193AC | - | 660-D-5001 | CONTROLLER | - | - | - | - | - | - | - | BPCS/SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660L5193 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660LAH5194 | - | 660-D-5001 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L5194 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660LAL5194 | - | 660-D-5001 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L5194 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660LT5194 | - | 660-D-5001 | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660L5194 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660LG5195 | 660LGR5195 | PRODUCT FRACTIONATOR RECEIVER | MAGNETIC GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660L5195 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | GS-RC-INS-200 / APPENDIX 14-T3 | CΙ2 / CΙ6 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | OTHER | OTHER | 0.66 | 4 | 40 | 120 | - | - | - | - | Group: 1 Phase: Gas | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-LG -5195-SP
- | - | - | - | 1 | - | 1 | - | 660LAL5294 | 660LAL2294 | 660-C-5001 | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | Note1 | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L5294 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660LSLL5294 | 660LSLL2294 | 660C5001 - 660LTS5294 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | Note1 | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L5294 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660LAX5294 | 660LDA2295 | 660C5001 - 660LTS5294 | SOFT CALCULATION | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L5294 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660LI5294 | 660LI2294 | 660C5001 - 660LTS5294 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660L5294 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660LTS5294 | 660LT2294 | PRODUCT FRACTIONATOR BOTTOM | GUIDED WAVE RADAR | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | 0 | 100 | - | % | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660L5294 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | GS-RC-INS-200 / APPENDIX 14_T4 | CΙ2 / CΙ6 (TBC) | P | LP | TV2 | STD RC INS 220 / FOLIO 45 | - | 0 | mm | - | 1950 | mm | - | 0 | mm | - | 1950 | mm | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS531/P05 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | OTHER | OTHER | 1.5 | 4.2 | 356 | 390 | - | - | - | - | - | - | - | - | - | ATEX | 2 | II | - | - | - | - | - | - | - | - | 660-LTS -5294-SP
- | - | - | - | 6 | - | 1 | - | 660LSHH5294 | - | 660C5001 - 660LTS5294 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | Note1 | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L5294 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660LAH5297 | 660LAH2297 | 660C5002 - 660FTS5297 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | Note2 | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L5297 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660LAL5297 | 660LAL2297 | 660-C-5002 | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | Note2 | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L5297 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660LSLL5297 | 660LALL2297 | 660C5002 - 660FTS5297 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660L5297 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660LAX5297 | 660LDA2298 | 660C5002 - 660FTS5297 | SOFT CALCULATION | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L5297 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660LI5297 | 660LI2297 | 660C5002 - 660FTS5297 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660L5297 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660LTS5297 | 660LTS2297 | 660-C-5002 | PRESSURE DP | - | - | W/T SEAL+CAPILLARY | - | - | L | ST1D | BPCS/SIS | S-PLC | - | 0 | 100 | - | % | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660L5297 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-430 / PART 1 FOLIO 2 | CI6 | NO | - | NI (NOT INSULATED) | Capillary 214359C-1000-STD-1576-0002-Pg5 | - | -5002.25 | mmH2O 4°C | - | -1896.95 | mmH2O 4°C | - | -10000 | mmH2O 4°C | - | 10000 | mmH2O 4°C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS530/P02 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | OTHER | OTHER | 1.1 | 4.1 | 247 | 310 | - | - | - | - | PED Group: 1 Phase Gas | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-LTS -5297-SP
- | - | - | - | 1 | - | 1 | - | 660LSH5299 | 660LAH2299 | 660-D-5002 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L5299 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660LAH5299 | 660-LAL -5299 | 660D5002 - 660LTS5299 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | Note:5 | - | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L5299 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660LSLL5299 | 660LALL2299 | 660D5002 - 660LTS5299 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | Note:5 | - | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L5299 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660LAX5299 | 660LDA2301 | 660D5002 - 660LTS5299 | SOFT CALCULATION | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L5299 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660LI5299 | 660LI2299 | 660D5002 - 660LTS5299 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660L5299 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660LTS5299 | 660LTS2299 | 660-D-5002 | PRESSURE DP | - | - | W/T SEAL+CAPILLARY | - | - | L | ST1D | BPCS/SIS | S-PLC | - | 0 | 100 | - | % | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660L5299 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-430 / PART 1 FOLIO 2 | CI6 | NO | - | NI (NOT INSULATED) | - | - | -1177 | mmH2O 4°C | - | -485.78 | mmH2O 4°C | - | -10000 | mmH2O 4°C | - | 10000 | mmH2O 4°C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS530/P03 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | OTHER | OTHER | 6.3 | 8 | 40 | 180 | - | - | - | - | PED Group: 1 Phase Gas | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-LTS -5299-SP
- | - | - | - | 1 | - | 1 | - | 660LT5301 | - | 660 D 5010 | PRESSURE DP | - | - | W/T SEAL+CAPILLARY | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0221 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660L5301 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660LI5301 | - | 660 D 5010 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0221 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660L5301 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660LG5302 | - | HOLD | MAGNETIC GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0221 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660L5302 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660LG5550 | - | 660 K 5001 COMPRESSOR | LEVEL GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660L5550 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | mm | - | 673 | mm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660LG5551 | - | 660 K 5001 COMPRESSOR | LEVEL GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660L5551 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | mm | - | 673 | mm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660LG5553A | - | 660 K 5001 COMPRESSOR | LEVEL GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660L5553 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | mm | - | 310 | mm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660LG5553B | - | 660 K 5001 COMPRESSOR | LEVEL GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660L5553 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | mm | - | 310 | mm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660LAL5554 | - | 660 K 5001 COMPRESSOR | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | Low Alarm (310 mm) | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660L5554 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660LI5554 | - | 660 K 5001 COMPRESSOR | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | Alarm L: 310 | - | - | - | 5 | 660L5554 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660LT5554 | - | 660 K 5001 COMPRESSOR | GUIDED WAVE RADAR | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 850 | Law Alarm (310 mm) | mm | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660L5554 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | - | - | - | - | - | - | - | - | - | - | - | - | 0 | mm | - | 900 | mm | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM515/P02 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | U660AAH5901_NTH2 | - | U660NTH25901 HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660NH25901 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | U660AAX5901_NTH2 | - | U660NTH25901 FAULT | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660NH25901 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | U660NTH2_5901 | - | 660-2 FLAME DETECTOR FOR (H2) | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 5 | 660NH25901 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | U660AAH5902_NTH2 | - | U660NTH25902 HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660NH25902 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | U660AAX5902_NTH2 | - | U660NTH25902 FAULT | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660NH25902 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | U660NTH2_5902 | - | 660-2 FLAME DETECTOR FOR (H2) | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 5 | 660NH25902 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | U660AAH5901_NTHC | - | U660NTHC5901 HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660NH5901 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | U660AAX5901_NTHC | - | U660NTHC5901 FAULT | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660NH5901 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | U660NTH_5901 | - | 660-2 FLAME DETECTOR FOR (HC) | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 5 | 660NH5901 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | U660AAH5902_NTHC | - | U660NTHC5902 HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660NH5902 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | U660AAX5902_NTHC | - | U660NTHC5902 FAULT | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660NH5902 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | U660NTH_5902 | - | 660-2 FLAME DETECTOR FOR (HC) | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 5 | 660NH5902 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | U660AAH1901_NTC | - | U660NTC1901 HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660NTC1901 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | U660AAX1901_NTC | - | U660NTC1901 FAULT | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660NTC1901 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | U660AAH5901_NTC | - | U660NTC5901 HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660NTC5901 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | U660AAX5901_NTC | - | U660NTC5901 FAULT | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660NTC5901 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | U660AAH5902_NTC | - | U660NTC5902 HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660NTC5902 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | U660AAX5902_NTC | - | U660NTC5902 FAULT | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660NTC5902 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | U660AAH5933_NTF | - | SMOKE DETECTOR | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660NTF5933 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | U660AAX5933_NTF | - | SMOKE DETECTOR | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660NTF5933 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660NTF_S5933 | - | SMOKE DETECTOR | SMOKE DETECTOR | - | - | 3 WIRES | N | - | AS | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 3 | 660NTF5933 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | U660AAH5981_NFT | - | U660NFT5981 HIGH | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660NTF5981 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | U660AAX5981_NFT | - | U660NFT5981 FAULT | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 8 | 660NTF5981 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660NTF_S5981 | - | 660-2 GAS DETECTOR SMOKE | SMOKE DETECTOR | - | - | 3 WIRES | N | - | AS | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 3 | 660NTF5981 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJGS592/ P01,P02 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660O2__5981 | - | 662 GAS DETECTOR (O2) | GAS DETECTOR O2 | - | - | - | - | - | AS | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 3 | 660O25981 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI50 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PT0004 | - | PT0004 TETE D0004 | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P0004 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PG0013 | - | DEBUTANIZER | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P0013 | R2D2 | - | - | - | - | - | TIP-660-5909-I | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 2 FOLIO 22 | CI6 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | -1 | bar | Gage | 9 | bar | Gage | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Group: 1 Phase: Gas | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PG0014 | - | DEBUTANIZER BOTTOM PUMP DISCHARGE | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P0014 | R2D2 | - | - | - | - | - | TIP-660-5508-I | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 2 FOLIO 8 | CI6 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | -1 | bar | Gage | 15 | bar | Gage | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-3"-P-25.1-B1F | - | - | - | - | - | - | - | - | - | - | Group: 1 Phase: Gas | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PG0015 | - | DEBUTANIZER BOTTOM PUMP DISCHARGE | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P0015 | R2D2 | - | - | - | - | - | TIP-660-5509-I | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 2 FOLIO 8 | CI6 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | -1 | bar | Gage | 15 | bar | Gage | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-3"-P-25.2-B1F | - | - | - | - | - | - | - | - | - | - | Group: 1 Phase: Gas | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PG0016 | - | PG0016 D0004 | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P0016 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PG0017 | - | DEBUTANIZER OVERHEAD PUMPS DISCHARGE | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P0017 | R2D2 | - | - | - | - | - | TIP-660-5912-I | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 4 FOLIO 2 | CI2 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | 0 | bar | Gage | 40 | bar | Gage | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-2"-P-2473.0-3BB1 | - | - | - | - | - | - | - | - | - | - | Group: 1 Phase: Gas | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PG0018 | - | DEBUTANIZER OVERHEAD PUMPS DISCHARGE | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P0018 | R2D2 | - | - | - | - | - | TIP-660-5913-I | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 4 FOLIO 2 | CI2 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | 0 | bar | Gage | 40 | bar | Gage | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-2"-P-2472.0-3BB1 | - | - | - | - | - | - | - | - | - | - | Group: 1 Phase: Gas | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PG0152 | - | DEBUTANIZER OVERHEAD PUMPS | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P0152 | R2D2 | - | - | - | - | - | TIP-660-5914-I | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 4 FOLIO 7 | CI2 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | -1 | bar | Gage | 9 | bar | Gage | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-3"-P-16.1-B1F | - | - | - | - | - | - | - | - | - | - | Group: 1 Phase: Gas | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PG0153 | - | DEBUTANIZER OVERHEAD PUMPS | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P0153 | R2D2 | - | - | - | - | - | TIP-660-5915-I | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 4 FOLIO 7 | CI2 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | -1 | bar | Gage | 9 | bar | Gage | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-3"-P-16.2-B1F | - | - | - | - | - | - | - | - | - | - | Group: 1 Phase: Gas | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PDG5029 | - | PRODUCT FRACTIONATOR REBOILER PUMPS STRAINER | PRESSURE DP GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5029 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2x STD-RC-INS-412 / PART 2 FOLIO 8 | CI6 | P | LP | TV2 | STD RC INS 220 / FOLIO 23 | - | - | - | - | - | - | - | 0 | mbar | Gage | 100 | mbar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-18"-P-2201.0-3BB3 | OTHER | L | 1.9 | 19 | 356 | 390 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PDG -5029-SP
- | - | - | - | 1 | - | 1 | - | 660PDG5030 | - | PRODUCT FRACTIONATOR REBOILER PUMPS STRAINER | PRESSURE DP GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5030 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2x STD-RC-INS-412 / PART 2 FOLIO 8 | CI6 | P | LP | TV2 | STD RC INS 220 / FOLIO 23 | - | - | - | - | - | - | - | 0 | mbar | Gage | 100 | mbar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-18"-2202.0-3BB3 | OTHER | L | 1.9 | 19 | 356 | 390 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PDG -5030-SP
- | - | - | - | 1 | - | 1 | - | 660PG5031 | - | PRODUCT FRACTIONATOR | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5031 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 2 FOLIO 22 | Cl6 | P | LP | TV2 | STD-RC-INS-220 / FOLIO 22 | - | - | - | - | - | - | - | -1 | bar | Gage | 3 | bar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | OTHER | OTHER | 1.7 | 4.2 | 361 | 390 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PG -5031-SP
- | - | - | - | 1 | - | 1 | - | 660PG5032 | - | PRODUCT FRACTIONATOR REBOILER PUMPS DISCHARGE | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5032 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 2 FOLIO 7 | Cl6 | P | LP | TV2 | STD RC INS 220 / FOLIO 23 | - | - | - | - | - | - | - | -1 | bar | Gage | 15 | bar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-10"-P-2009.0-3BB3 | OTHER | L | 9.1 | 19 | 357 | 390 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PG -5032-SP
- | - | - | - | 1 | - | 1 | - | 660PG5033 | - | PRODUCT FRACTIONATOR REBOILER PUMPS DISCHARGE | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5033 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 2 FOLIO 7 | Cl6 | P | LP | TV2 | STD RC INS 220 / FOLIO 23 | - | - | - | - | - | - | - | -1 | bar | Gage | 15 | bar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-10"-P-2203.0-3BB3 | OTHER | L | 9.1 | 19 | 357 | 390 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PG -5033-SP
- | - | - | - | 1 | - | 1 | - | 660PG5034 | - | KEROSENE STRIPPER OVERHEAD | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5034 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 2 FOLIO 8 | Cl6 | NO | - | CC | - | - | - | - | - | - | - | - | -1 | bar | Gage | 1.5 | bar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-8"-P-2011.0-1BB1 | KERO | OTHER | 0.84 | 4 | 216 | 310 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PG -5034-SP
- | - | - | - | 1 | - | 1 | - | 660PG5035 | - | KEROSENE PRODUCT PUMP DISCHARGE | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5035 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 2 FOLIO 8 | Cl6 | NO | - | CC | - | - | - | - | - | - | - | - | -1 | bar | Gage | 15 | bar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-4"-P-2016.0-3BB3 | KERO | L | 7.2 | 19 | 248 | 280 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PG -5035-SP
- | - | - | - | 1 | - | 1 | - | 660PG5036 | - | KEROSENE PRODUCT PUMP DISCHARGE | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5036 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 2 FOLIO 8 | Cl6 | NO | - | CC | - | - | - | - | - | - | - | - | -1 | bar | Gage | 15 | bar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-4"-P-2206.0-3BB3 | KERO | L | 7.2 | 19 | 248 | 280 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PG -5036-SP
- | - | - | - | 1 | - | 1 | - | 660PDG5037 | - | KEROSENE PRODUCT PUMP STRAINER | PRESSURE DP GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5037 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2x STD-RC-INS-412 / PART 2 FOLIO 8 | CI6 | NO | - | CC | - | - | - | - | - | - | - | - | 0 | mbar | Gage | 100 | mbar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2017.0-3BB3 | KERO | L | 1.1 | 19 | 247 | 280 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PDG -5037-SP
- | - | - | - | 1 | - | 1 | - | 660PDG5038 | - | KEROSENE PRODUCT PUMP STRAINER | PRESSURE DP GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5038 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2x STD-RC-INS-412 / PART 2 FOLIO 8 | CI6 | NO | - | CC | - | - | - | - | - | - | - | - | 0 | mbar | Gage | 100 | mbar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2018.0-3BB3 | KERO | L | 1.1 | 19 | 247 | 280 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PDG -5038-SP
- | - | - | - | 1 | - | 1 | - | 660PG5045 | - | 660-G-5002A SUCTION | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | 0 | 350 | - | C | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5045 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 2 FOLIO 7 | Cl6 | NO | - | CC | - | - | - | - | - | - | - | - | -1 | bar | Gage | 3 | bar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2017.0-3BB3 | KERO | L | 1.1 | 19 | 248 | 280 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PG -5045-SP
- | - | - | - | 1 | - | 1 | - | 660PG5046 | - | 660-G-5002B SUCTION | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5046 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 2 FOLIO 7 | Cl6 | NO | - | CC | - | - | - | - | - | - | - | - | -1 | bar | Gage | 3 | bar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2018.0-3BB3 | KERO | L | 1.1 | 19 | 248 | 280 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PG -5046-SP
- | - | - | - | 1 | - | 1 | - | 660PG5055 | - | DEBUTANIZER BOTTOM COOLER | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5055 | R2D2 | - | - | - | - | - | TIP-660-5510-I | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 2 FOLIO 7 | CI6 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | -1 | bar | Gage | 5 | bar | Gage | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-28.1-B1 | - | - | - | - | - | - | - | - | - | - | Group: 1 Phase: Gas | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PSV5060 | - | FROM 660 E 5005 | RELIEF VALVE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0201 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5060 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CC | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2014.0-3BB3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PSV5062A | 660PRV5062A | Fractionator off-gas KOD 660-D-5002 | RELIEF VALVE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5062A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2088.0-1BB1 | OTHER | OTHER | - | 8 | - | 180 | - | - | - | - | IV | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PSV -5062A-SP
- | - | - | - | 1 | - | 1 | - | 660PSV5062B | 660PRV5062B | Fractionator off-gas KOD 660-D-5002 | RELIEF VALVE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5062B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2088.0-1BB1 | OTHER | OTHER | - | 8 | - | 180 | - | - | - | - | IV | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PSV -5062B-SP
- | - | - | - | 1 | - | 1 | - | 660PSV5063 | - | 660-E-5008 Tube Side | RELIEF VALVE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0216 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5063 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-2"-P-2016.4-3BB3 | OTHER | OTHER | - | 19 | - | 280 | - | - | - | - | IV | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PSV -5063-SP
- | - | - | - | 1 | - | 1 | - | 660PG5078 | - | 660-G-5001A SUCTION | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5078 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 2 FOLIO 7 | Cl6 | P | LP | TV2 | STD RC INS 220 / FOLIO 23 | - | - | - | - | - | - | - | -1 | bar | Gage | 5 | bar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-18"-P-2201.0-3BB3 | OTHER | L | 1.8 | 19 | 357 | 390 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PG -5078-SP
- | - | - | - | 1 | - | 1 | - | 660PG5079 | - | 660-G-5001B SUCTION | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5079 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 2 FOLIO 7 | Cl6 | P | LP | TV2 | STD RC INS 220 / FOLIO 23 | - | - | - | - | - | - | - | -1 | bar | Gage | 5 | bar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-18"-2202.0-3BB3 | OTHER | L | 1.8 | 19 | 357 | 390 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PG -5079-SP
- | - | - | - | 1 | - | 1 | - | 660PAH5081 | - | FROM 660 C 5001 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5081 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660PAL5081 | - | FROM 660 C 5001 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5081 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660PI5081 | - | FROM 660 C 5001 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660P5081 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660PT5081 | - | FROM 660 C 5001 | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5081 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD RC INS 410_PART 3_FOLIO 2 | - | - | - | - | - | - | 0 | bar | - | 1.56 | bar | - | 0 | bar | - | 10 | bar | - | - | - | - | - | - | - | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-24"-P-2002.0-1BB1 | - | - | - | - | - | - | - | - | - | - | (Note 1) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PSV5082A | - | Product Fractionator 660-C-5001 | RELIEF VALVE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5082A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | PP | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-12"-P-2002.1-1BB1 | OTHER | OTHER | - | 3.5 | - | 390 | - | - | - | - | IV | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PSV -5082A-SP
- | - | - | - | 1 | - | 1 | - | 660PSV5082B | - | Product Fractionator 660-C-5001 | RELIEF VALVE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5082B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | PP | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-12"-P-2002.1-1BB1 | OTHER | OTHER | - | 3.5 | - | 390 | - | - | - | - | IV | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PSV -5082B-SP
- | - | - | - | 1 | - | 1 | - | 660PSV5082C | - | Product Fractionator 660-C-5001 | RELIEF VALVE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5082C | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | PP | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-12"-P-2002.1-1BB1 | OTHER | OTHER | - | 3.5 | - | 390 | - | - | - | - | IV | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PSV -5082C-SP
- | - | - | - | 1 | - | 1 | - | 660PSV5082D | - | Product Fractionator 660-C-5001 | RELIEF VALVE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5082D | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-12"-P-2002.1-1BB1 | OTHER | OTHER | - | 3.5 | - | 390 | - | - | - | - | IV | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-PSV -5082D-SP
- | - | - | - | 1 | - | 1 | - | 660PSV5082E | - | Product Fractionator 660-C-5001 | RELIEF VALVE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5082E | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | IV | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PSV5082F | - | Product Fractionator 660-C-5001 | RELIEF VALVE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5082F | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | IV | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PI5083 | - | FROM 660C5001 - 660PT5083 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660P5083 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | 660PT5150 | - | INLET PASS TO REBOILER 660 F 5001 | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 20 | - | bar Gag | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5150 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 2 FOLIO 3 | CI2 | P | LP | TV2 | STD RC INS 220 / FOLIO 21 | - | 0 | bar | Gage | 20 | bar | Gage | -1 | bar | Gage | 35 | bar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM531/P16 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-10"-P-2009.1-3BB3 | OTHER | L | 8.77 | 19 | 357 | 390 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PT -5150-SP
- | - | - | - | 3 | - | 1 | - | 660PSV5083 | - | 660-E-5005 Tube Side | RELIEF VALVE | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5083 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 /CI10 | P | LP | TV2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-2"-P-2009.5-3BB3 | OTHER | OTHER | - | 19 | - | 390 | - | - | - | - | IV | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PSV -5083-SP
- | - | - | - | 1 | - | 1 | - | 660PDAL5084 | 660FAL5084 | FROM 660 F 5001 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5084 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660PDC5084 | 660FC5084 | FROM 660F5001 - 660PDT5084 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660P5084 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660PDE5084 | 660FE5084 | Product Fractionator Reboiler Vaporization | ORIFICE | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660P5084 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | LP | TV2 | - | - | 0 | mbar | - | 245 | mbar | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-20"-P-2010.0-3BB3 | OTHER | OTHER | 1.8 | 5.2 | 364.3 | 390 | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PDE -5084-SP
- | - | - | - | 4 | - | 1 | - | 660TT5020 | - | PRODUCT FRACTIONATOR REBOILER | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 400 | - | °C | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5020 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 2 | - | NO | - | CC | - | - | 0 | °C | - | 400 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM532/P07 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-20"-P-2010.0-3BB3 | OTHER | OTHER | 1.7 | 5.2 | 361 | 390 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5020-SP
- | - | - | - | 5 | - | 1 | - | 660PDY5084A | - | DISCHARGE 660K5001 | SOFT CALCULATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660P5084 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660PDY5084B | - | DISCHARGE 660K5001 | SOFT CALCULATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660P5084 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PSV5084A | - | 660-K-5001 Discharge | RELIEF VALVE | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5084A | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2035.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PSV5084B | - | 660-K-5001 Discharge | RELIEF VALVE | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5084B | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2035.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PDC5085 | - | FROM 660G5001AB - 660PDT5085 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660P5085 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | CV01 | - | 3 | - | 1 | - | 660PDV5085 | - | 660 E 5005 BY-PASS | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5085 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA004 | CI1/CI9/CI10 | P | LP | TV2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM530/P13 | - | E10201 | 660IADM515/05 | - | - | - | - | - | - | - | - | 660-6"-P-2009.4-3BB3 | OTHER | L | 9.01 | 19 | 352 | 390 | - | - | - | - | III module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PDV -5085-SP
- | - | - | - | 3 | - | 1 | - | 660TT5023 | - | KEROSENE STRIPPER | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 350 | - | C | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5023 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 2 | - | NO | - | CC | - | - | 0 | °C | - | 350 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM530/P14 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-8"-P-2011.0-1BB1 | OTHER | OTHER | 0.92 | 4 | 216 | 310 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5023-SP
- | - | - | - | 1 | - | 1 | - | 660PDT5086 | 660-PDT -5080 | HOLD | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5086 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | HOLD | NO | - | CC | - | - | - | - | - | - | - | - | - | bar | - | 10 | - | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-18"-P-2010.0-3BB3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660PDI5086 | - | HOLD | DIFFERENTIAL PRESSURE INDICATOR | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660P5086 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660PDAL5086 | 660-PDAL -5080 | HOLD | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5086 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660PDT5186 | - | DEBUTANIZER REBOILER BYPASS | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 4 | - | % | 214359C-6602-PID-0021-0216 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5186 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-411 / PART 2 FOLIO 11 | CI6 | NO | - | CC | - | - | 0 | bar | - | 4 | bar | - | -5000 | mbar | - | 5000 | mbar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM534/P13 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-2"-P-2016.3-3BB3 | KERO | L | 8.68 | 19 | 248 | 280 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PDT -5186-SP
- | - | - | - | 1 | - | 1 | - | 660PSV5113 | - | API PLAN PUMP 660G5001A | RELIEF VALVE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5113 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | - | - | - | PP | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | IV | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PSV5114 | - | API PLAN PUMP 660G5001A | RELIEF VALVE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5114 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | - | - | - | PP | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | IV | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | CV01 | - | 4 | - | 1 | - | 660PDV5186 | - | 660 E 5008 BYPASS | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0216 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5186 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA004 | CI1/CI9 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM534/P14 | - | E10201 | 660IADM517/03 | - | - | - | - | - | - | - | - | 660-2"-P-2016.3-3BB3 | OTHER | L | 7.33 | 19 | 244 | 280 | - | - | - | - | III module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PDV -5186-SP
- | - | - | - | 1 | - | 1 | - | 660PDT5118 | - | FRACTIONATOR OFF-GAS COMPRESSOR SUCTION | PRESSURE DP | - | - | - | - | - | L | ST1D | BPCS | DCS | - | -0.5 | 1 | - | bar | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5118 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-411 / PART 3 FOLIO 11 | CI6 | P | LP | TV3 | STD RC INS 220 / FOLIO 28 | - | -0.5 | bar | - | 1 | bar | - | -5000 | mbar | - | 5000 | mbar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM533/P01 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-14"-P-2028.0-1BB1 | OTHER | OTHER | 0.4 | 4 | 40 | 160 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PDT -5118-SP
- | - | - | - | 2 | - | 1 | - | 660PDI5118 | - | FRACTIONATOR OFF-GAS COMPRESSOR SUCTION - 660PDT5118 | DIFFERENTIAL PRESSURE INDICATOR | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660P5118 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PDG5129 | - | PRODUCT FRACTIONATOR OVERHEAD PUMPS STRAINER | PRESSURE DP GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5129 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2x STD-RC-INS-412 / PART 2 FOLIO 8 | CI6 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | 0 | mbar | Gage | 100 | mbar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-10"-P-2208.0-1BB1 | OTHER | L | 0.7 | 12.5 | 40 | 120 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PDG -5129-SP
- | - | - | - | 1 | - | 1 | - | 660PG5130 | - | HOLD | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5130 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-10"-P-2209.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660PDG5130 | - | PRODUCT FRACTIONATOR OVERHEAD PUMPS STRAINER | PRESSURE DP GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5130 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2x STD-RC-INS-412 / PART 2 FOLIO 8 | CI6 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | 0 | mbar | Gage | 100 | mbar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-10"-P-2209.0-1BB1 | OTHER | L | -0.7 | 12.5 | 40 | 120 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PDG -5130-SP
- | - | - | - | 1 | - | 1 | - | 660PG5131 | - | PRODUCT FRACTIONATOR RECEIVER | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5131 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 2 FOLIO 8 | Cl6 | P | LP | TV3 | STD RC INS 220 / FOLIO 23 | - | - | - | - | - | - | - | -1 | bar | Gage | 1.5 | bar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-14"-P-2028.0-1BB1 | OTHER | OTHER | 0.4 | 4 | 40 | 160 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PG -5131-SP
- | - | - | - | 1 | - | 1 | - | 660PG5132 | - | PRODUCT FRACTIONATOR OVERHEAD PUMPS DISCHARGE | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5132 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 2 FOLIO 8 | Cl6 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | -1 | bar | Gage | 9 | bar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2032.0-1BB1 | OTHER | L | 7.2 | 12.5 | 41 | 120 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PG -5132-SP
- | - | - | - | 1 | - | 1 | - | 660PG5133 | - | PRODUCT FRACTIONATOR OVERHEAD PUMPS DISCHARGE | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5133 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 2 FOLIO 8 | Cl6 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | -1 | bar | Gage | 9 | bar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2210.0-1BB1 | OTHER | L | 7.2 | 12.5 | 41 | 120 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PG -5133-SP
- | - | - | - | 1 | - | 1 | - | 660PG5135 | - | FRACTIONATOR OFF-GAS KNOCKOUT DRUM | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5135 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 2 FOLIO 7 | Cl6 | P | LP | TV3 | STD RC INS 220 / FOLIO 23 | - | - | - | - | - | - | - | -1 | bar | Gage | 9 | bar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-3"-P-2037.1-1BB1 | OTHER | OTHER | 6.2 | 8 | 40 | 180 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PG -5135-SP
- | - | - | - | 1 | - | 1 | - | 660PG5138 | - | 660-G-5003A SUCTION | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5138 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 2 FOLIO 7 | Cl6 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | -1 | bar | Gage | 1.5 | bar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-10"-P-2208.0-1BB1 | OTHER | L | 0.7 | 12.5 | 41 | 120 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PG -5138-SP
- | - | - | - | 1 | - | 1 | - | 660PG5139 | - | 660-G-50003B SUCTION | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5139 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 2 FOLIO 7 | Cl6 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | -1 | bar | Gage | 1.5 | bar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-10"-P-2209.0-1BB1 | OTHER | L | 0.7 | 12.5 | 41 | 120 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PG -5139-SP
- | - | - | - | 3 | - | 1 | - | 660PT5301 | - | NATURAL GAS TO 660 F 5001 BURNERS | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 4 | - | bar Gage | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5301 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 3 | CI2 | NO | - | CC | - | - | 0 | bar | Gage | 4 | bar | Gage | -1 | bar | Gage | 35 | bar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM531/P17 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-4"-FG-2222.0-1KB2 | GN | OTHER | 2 | 3.5 | 41 | 75 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PT -5301-SP
- | - | - | - | 1 | - | 1 | - | 660PI5150 | 660-FI -5150 | INLET PASS TO REBOILER 660F5001 - 660PT5150 | PRESSURE INDICATOR | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660P5150 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PG5165 | - | API PLAN PUMP 660G5001A | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5165 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PG5167 | - | API PLAN PUMP 660G5001A | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5167 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PC5180 | - | FROM 660C5001 - 660PT5180 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660P5180 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660PT5235 | - | NATURAL GAS FROM OSBL | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 4 | - | bar Gage | 214359C-6602-PID-0041-0002 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5235 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 3 | CI2 | NO | - | CC | - | - | 0 | bar | Gage | 4 | bar | Gage | -1 | bar | Gage | 35 | bar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM536/P12 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-3"-FG-2081.0-1BB1 | GN | OTHER | 2.9 | 3.5 | 41 | 75 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PT -5235-SP
- | - | - | - | 1 | - | 1 | - | 660PC5181A | 660PC5182 | FROM 660D5001 - 660PT5181 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660P5181 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660PC5181B | - | TO 660K5001 - 660PT5181 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660P5181 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV15 | - | 11 | - | 1 | - | 660PT5001 | 660-PT -5011 | PRESS. ON VALVE INS AIR ACCUMULATOR | PRESSURE REL | - | - | - | - | - | L | ST1D | SIS | DCS | - | 0 | 10 | - | bar Gage | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660U5001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA020 | CI2 | NO | - | NI (NOT INSULATED) | - | - | 0 | bar | Gage | 10 | bar | - | -1 | bar | Gage | 35 | bar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM533/P02 | - | E10201 | - | - | - | - | - | - | - | - | - | ACCU | OTHER | OTHER | 6.3 | 9 | 40 | 70 | - | - | - | - | PED Group: 2 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PT -5001-SP
- | - | UV15 | - | 11 | - | 1 | - | 660PT5002 | - | PRESS. ON VALVE INS AIR ACCUMULATOR | PRESSURE REL | - | - | - | - | - | L | ST1D | SIS | DCS | - | 0 | 10 | - | bar Gage | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660U5002 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA020 | CI2 | NO | - | NI (NOT INSULATED) | - | - | 0 | bar | Gage | 10 | bar | - | -1 | bar | Gage | 35 | bar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM533/P03 | - | E10201 | - | - | - | - | - | - | - | - | - | ACCU | OTHER | OTHER | 6.3 | 9 | 40 | 70 | - | - | - | - | PED Group: 2 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PT -5002-SP
- | - | - | - | 3 | - | 1 | - | 660PT5181 | - | PRODUCT FRACTIONATOR RECEIVER | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -0.5 | 1 | - | bar Gage | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5181 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 11 | CI6 | P | LP | TV3 | STD RC INS 220 / FOLIO 23 | - | -0.5 | bar | Gage | 1 | bar | Gage | -1 | bar | Gage | 5 | bar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM533/P04 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-14"-P-2028.0-1BB1 | OTHER | OTHER | 0.4 | 4 | 40 | 160 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PT -5181-SP
- | - | - | - | 2 | - | 1 | - | 660PY5182 | 660PY5180A | FROM 660D5001 - 660PT5180/5181 | SOFT CALCULATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660P5182 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PC5183 | - | TO FRACTIONATOR OFFGAS LPG RECOVERY - 660PT5183 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660P5183 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660PT5183 | - | FRACTIONATOR OFF-GAS KNOCKOUT DRUM | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 10 | - | bar Gage | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5183 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 3 | CI2 | P | LP | TV3 | STD RC INS 220 / FOLIO 21 | - | 0 | bar | Gage | 10 | bar | Gage | -1 | bar | Gage | 35 | bar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM538/P04 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-3"-P-2037.1-1BB1 | OTHER | OTHER | 6.2 | 8 | 40 | 180 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PT -5183-SP
- | - | CV01 | - | 3 | - | 1 | - | 660PV5183 | - | FRACTIONATOR OFFGAS TO LPG RECOVERY | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5183 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA004 | CI1/CI9 | P | LP | TV3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM538/P05 | - | E10201 | 660IADM515/06 | - | - | - | - | - | - | - | - | 660-3"-P-2037.1-1BB1 | OTHER | OTHER | 6.06 | 8 | 40 | 180 | - | - | - | - | III module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PV -5183-SP
- | - | - | - | 4 | - | 1 | - | 660PY5183A | - | TO FRACTIONATOR OFFGAS LPG RECOVERY - 660PT5183 | SOFT CALCULATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660P5183 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660PY5183B | - | TO FRACTIONATOR OFFGAS LPG RECOVERY - 660PT5183 | SOFT CALCULATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660P5183 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PTS5184A | - | FRACTIONATOR OFF-GAS COMPRESSOR SUCTION | PRESSURE REL | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | -0.5 | 1 | - | bar gage | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5184 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 11 | CI6 | P | LP | TV3 | STD RC INS 220 / FOLIO 23 | - | -0.5 | bar | Gage | 1 | bar | Gage | -1 | bar | Gage | 5 | bar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS533/P03 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-14"-P-2028.0-1BB1 | OTHER | OTHER | 0.4 | 4 | 40 | 160 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PTS -5184A-SP
- | - | - | - | 2 | - | 1 | - | 660PTS5184B | - | FRACTIONATOR OFF-GAS COMPRESSOR SUCTION | PRESSURE REL | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | -0.5 | 1 | - | bar gage | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5184 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 11 | CI6 | P | LP | TV3 | STD RC INS 220 / FOLIO 23 | - | -0.5 | bar | Gage | 1 | bar | Gage | -1 | bar | Gage | 5 | bar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS533/P04 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-14"-P-2028.0-1BB1 | OTHER | OTHER | 0.4 | 4 | 40 | 160 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PTS -5184B-SP
- | - | - | - | 3 | - | 1 | - | 660PTS5184C | - | FRACTIONATOR OFF-GAS COMPRESSOR SUCTION | PRESSURE REL | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | -0.5 | 1 | - | bar gage | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5184 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 11 | CI6 | P | LP | TV3 | STD RC INS 220 / FOLIO 23 | - | -0.5 | bar | Gage | 1 | bar | Gage | -1 | bar | Gage | 5 | bar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS539/P02 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-14"-P-2028.0-1BB1 | OTHER | OTHER | 0.4 | 4 | 40 | 160 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PTS -5184C-SP
- | - | - | - | 4 | - | 1 | - | 660PI5184A | - | FROM 660D5001 - 660PTS5184ABC | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | Alarm L: 0.2 - 0.53 barg Alarm LL: 0.1 - 0.45 barg | - | - | - | 5 | 660P5184 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660PI5184B | - | FROM 660D5001 - 660PTS5184ABC | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | Alarm L: 0.2 - 0.53 barg Alarm LL: 0.1 - 0.45 barg | - | - | - | 5 | 660P5184 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660PI5184C | - | FROM 660D5001 - 660PTS5184ABC | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | Alarm L: 0.2 - 0.53 barg Alarm LL: 0.1 - 0.45 barg | - | - | - | 5 | 660P5184 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 1 | - | 660PSLL5184A | 660PAHH5184 | FROM 660D5001 - 660PTS5184ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | 0 | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5184 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 1 | - | 660PSLL5184B | - | FROM 660D5001 - 660PTS5184ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | Low Alarm (0) | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660P5184 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 9 | - | 1 | - | 660PSLL5184C | - | FROM 660D5001 - 660PTS5184ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | Low Alamr (0.2) | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660P5184 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 10 | - | 1 | - | 660PALL5184 | - | FROM 660D5001 - 660PTS5184ABC | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | Low-Low Alarm (0) | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5184 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 11 | - | 1 | - | 660PAX5184 | - | FROM 660D5001 - 660PTS5184ABC | ALARM | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5184 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 12 | - | 1 | - | 660PSL5184 | - | FROM 660D5001 - 660PTS5184ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1C | SIS | DCS | - | - | - | 0.2 | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5184 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 13 | - | 1 | - | 660PAL5184 | - | FROM 660D5001 - 660PTS5184ABC | ALARM | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - | - | - | Low Alarm (0.2) | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5184 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PTS5185A | - | FRACTIONATOR OFF-GAS COMPRESSOR DISCHARGE | PRESSURE REL | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | 0 | 10 | - | bar gage | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5185 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 11 | CI6 | NO | - | PP | - | - | 0 | bar | Gage | 10 | bar | Gage | -1 | bar | Gage | 35 | bar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS533/P05 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-6"-P-2035.0-1BB1 | OTHER | OTHER | 6.7 | 8.5 | 179 | 200 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PTS -5185A-SP
- | - | - | - | 2 | - | 1 | - | 660PTS5185B | - | FRACTIONATOR OFF-GAS COMPRESSOR DISCHARGE | PRESSURE REL | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | 0 | 10 | - | bar gage | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5185 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 11 | CI6 | NO | - | PP | - | - | 0 | bar | Gage | 10 | bar | Gage | -1 | bar | Gage | 35 | bar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS533/P06 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-6"-P-2035.0-1BB1 | OTHER | OTHER | 6.7 | 8.5 | 179 | 200 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PTS -5185B-SP
- | - | - | - | 3 | - | 1 | - | 660PTS5185C | - | FRACTIONATOR OFF-GAS COMPRESSOR DISCHARGE | PRESSURE REL | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | 0 | 10 | - | bar gage | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5185 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 11 | CI6 | NO | - | PP | - | - | 0 | bar | Gage | 10 | bar | Gage | -1 | bar | Gage | 35 | bar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS539/P03 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-6"-P-2035.0-1BB1 | OTHER | OTHER | 6.7 | 8.5 | 179 | 200 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PTS -5185C-SP
- | - | - | - | 4 | - | 1 | - | 660PI5185A | - | TO 660E5007 - 660PTS5185ABC | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | Alarm HH: 7.35 Alarm H: 7 Alarm L: 5.5 | - | - | - | 5 | 660P5185 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660PI5185B | - | TO 660E5007 - 660PTS5185ABC | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | Alarm HH: 7.35 Alarm H: 7 Alarm L: 5.5 | - | - | - | 5 | 660P5185 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660PI5185C | - | TO 660E5007 - 660PTS5185ABC | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | Alarm HH: 7.35 Alarm H: 7 Alarm L: 5.5 | - | - | - | 5 | 660P5185 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 1 | - | 660PSHH5185A | 660-PAHH -5185 | TO 660E5007 - 660PTS5185ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | High High: Alarm (7.7) | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5185 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 1 | - | 660PSHH5185B | - | TO 660E5007 - 660PTS5185ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | High High: Alarm (7.7) | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660P5185 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 9 | - | 1 | - | 660PSHH5185C | - | TO 660E5007 - 660PTS5185ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | High High: Alarm (7.7) | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660P5185 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 10 | - | 1 | - | 660PAHH5185 | - | TO 660E5007 - 660PTS5185ABC | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | High High Alarm (7.7) | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5185 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 11 | - | 1 | - | 660PAX5185 | - | TO 660E5007 - 660PTS5185ABC | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5185 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 12 | - | 1 | - | 660PSH5185B | - | TO 660E5007 - 660PTS5185ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1C | SIS | DCS | - | - | - | High Alamr (7.20) | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5185 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 13 | - | 1 | - | 660PAH5185A | - | TO 660E5007 - 660PTS5185ABC | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | High Alamr (7.20) | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5185 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PDAH5186 | - | TO 660-E-0003 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0216 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5186 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660PDC5186 | - | TO 660E0003 - 660PDT5186 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0216 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660P5186 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PT5112 | - | API PLAN PUMP 660G5001A | PRESSURE TRANSMITTER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -1 | 35 | Alarm High (10.6) Alarm Law (7.1) | barG | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5112 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM534/P15 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PT5115 | - | API PLAN PUMP 660G5001A | PRESSURE TRANSMITTER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -1 | 35 | Alarm Low (7.1) Alarm High (10.6) | barG | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5115 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM534/P16 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PDT5187 | - | HOLD | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0216 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5187 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CC | - | - | - | - | - | - | - | - | - | bar | - | 30 | - | - | - | - | - | - | - | - | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PT5212 | - | API PLAN PUMP 660G5001B | PRESSURE TRANSMITTER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -1 | 35 | Alarm Low (7.1) Alarm High (10.6) | barG | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5212 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM534/P17 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PSV5213 | - | API PLAN PUMP 660G5001B | RELIEF VALVE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5213 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | - | - | - | PP | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | IV | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PSV5214 | - | API PLAN PUMP 660G5001B | RELIEF VALVE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5214 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | - | - | - | PP | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | IV | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PT5215 | - | API PLAN PUMP 660G5001B | PRESSURE TRANSMITTER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -1 | 35 | Alarm Low (7.1) Alarm High (10.6) | barG | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5215 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM534/P18 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5127 | - | DEBUTANIZER REBOILER | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 200 | - | c | 214359C-6602-PID-0021-0216 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5127 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 2 | - | NO | - | CC | - | - | 0 | °C | - | 200 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM534/P19 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-8"-P-2048.0-1BB1 | OTHER | L | 4.46 | 11.5 | 126 | 160 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5127-SP
- | - | - | - | 1 | - | 1 | - | 660PTS5226A | 660PTS2226A | FRACTIONATOR OVERHEAD | PRESSURE REL | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | -0.5 | 2 | - | bar Gage | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5226 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 11 | CI6 | NO | - | PP | - | - | -0.5 | bar | Gage | 2 | bar | Gage | -1 | bar | Gage | 35 | bar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS540/P03 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-24"-P-2002.0-1BB1 | OTHER | OTHER | 0.78 | 3.5 | 109 | 145 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PTS -5226A-SP
- | - | - | - | 2 | - | 1 | - | 660PTS5226B | 660PTS5226B | FRACTIONATOR OVERHEAD | PRESSURE REL | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | -0.5 | 2 | - | bar Gage | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5226 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 11 | CI6 | NO | - | PP | - | - | -0.5 | bar | Gage | 2 | bar | Gage | -1 | bar | Gage | 35 | bar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS531/P06 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-24"-P-2002.0-1BB1 | OTHER | OTHER | 0.78 | 3.5 | 109 | 145 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PTS -5226B-SP
- | - | - | - | 3 | - | 1 | - | 660PTS5226C | 660PTS2226C | FRACTIONATOR OVERHEAD | PRESSURE REL | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | -0.5 | 2 | - | bar Gage | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5226 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 11 | CI6 | NO | - | PP | - | - | -0.5 | bar | Gage | 2 | bar | Gage | -1 | bar | Gage | 35 | bar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS531/P07 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-24"-P-2002.0-1BB1 | OTHER | OTHER | 0.78 | 3.5 | 109 | 145 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PTS -5226C-SP
- | - | - | - | 4 | - | 1 | - | 660PI5226A | 660PI2226A | FROM 660C5001 - 660PTS5226ABC | INDICATION | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660P5226 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660PI5226B | 660PI2226B | FROM 660C5001 - 660PTS5226ABC | INDICATION | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660P5226 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660PI5226C | 660PI2226C | FROM 660C5001 - 660PTS5226ABC | INDICATION | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660P5226 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 1 | - | 660PSHH5226A | - | FROM 660C5001 - 660PTS5226ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | High Alarm (1.3) / High-High Alarm (1.8) | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5226 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 1 | - | 660PSHH5226B | - | FROM 660C5001 - 660PTS5226ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | High Alarm (1.3) / High-High Alarm (1.8) | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660P5226 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 9 | - | 1 | - | 660PSHH5226C | - | FROM 660C5001 - 660PTS5226ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | High Alarm (1.3) / High-High Alarm (1.8) | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660P5226 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 10 | - | 1 | - | 660PSLL5226A | 660-PSLL -5226 | FROM 660C5001 - 660PTS5226ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | Low Alarm (0.3)Low-Low Alarm (0.1) | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5226 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 11 | - | 1 | - | 660PSLL5226B | - | FROM 660C5001 - 660PTS5226ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | Low Alarm (0.3)Low-Low Alarm (0.1) | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660P5226 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 12 | - | 1 | - | 660PSLL5226C | - | FROM 660C5001 - 660PTS5226ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | Low Alarm (0.3)Low-Low Alarm (0.1) | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660P5226 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 13 | - | 1 | - | 660PAHH5226 | - | FROM 660C5001 - 660PTS5226ABC | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | High High Alarm (1.8) | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5226 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 14 | - | 1 | - | 660PALL5226 | - | FROM 660C5001 - 660PTS5226ABC | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | Low Low Alarm (1.0 barg) | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5226 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 15 | - | 1 | - | 660PAX5226 | 660PDA2227 | FROM 660C5001 - 660PTS5226ABC | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5226 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 16 | - | 1 | - | 660PSH5226 | - | FROM 660C5001 - 660PTS5226ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1C | SIS | DCS | - | - | - | 1.3 | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660P5226 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 17 | - | 1 | - | 660PSL5226 | - | FROM 660C5001 - 660PTS5226ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1C | SIS | DCS | - | - | - | 0.3 | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660P5226 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 18 | - | 1 | - | 660PAH5226 | 660PAH2226 | FROM 660C5001 - 660PTS5226ABC | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | High Alarm (1.3) | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5226 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 19 | - | 1 | - | 660PAL5226 | 660PAL2226 | FROM 660C5001 - 660PTS5226ABC | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | Low Alarm(0.3 barg) | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5226 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 20 | - | 1 | - | 660PDY5226 | 660PDY5082 | FROM 660C5001 - 660PTS5226ABC | SOFT CALCULATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660P5226 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 21 | - | 1 | - | 660PDI5226 | 660PDI5082 | FROM 660C5001 - 660PTS5226ABC | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660P5226 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660PSHH5230 | - | FROM 660E5008 - 660PTS5230 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | 4.6 | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5230 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660PI5230 | - | FROM 660E5008 - 660PTS5230 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660P5230 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660PTS5230 | 660PTS2230 | DEBUTANIZER | PRESSURE REL | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | -0.5 | 5 | - | bar gage | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5230 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 11 | CI6 | NO | - | NI (NOT INSULATED) | - | - | -0.5 | bar | Gage | 5 | bar | Gage | -1 | bar | Gage | 35 | bar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS534/P03 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-3/4"-P-12.1-1BB1 | OTHER | OTHER | 4.1 | 4.8 | 53 | 160 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PTS -5230-SP
- | - | - | - | 5 | - | 1 | - | 660PAX5230 | - | FROM 660E5008 - 660PTS5230 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660P5230 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PAH5233 | 660-PAH -5230 | DEBUTANIZER - 660PT5233 | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | High Alarm (4.3) | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5233 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660PI5233 | - | DEBUTANIZER - 660PT5233 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660P5233 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660PT5233 | - | DEBUTANIZER | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS/SIS | DCS | - | 0 | 5 | - | bar Gage | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5233 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 11 | CI6 | NO | - | NI (NOT INSULATED) | - | - | 0 | bar | Gage | 5 | bar | Gage | -1 | bar | Gage | 35 | bar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM535/P06 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-10"-P-2044.0-1BB1 | OTHER | OTHER | 4.1 | 4.8 | 53 | 160 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PTS -5233-SP
- | - | - | - | 1 | - | 1 | - | 660PI5234 | - | LP STEAM FROM OSBL - 660PT5234 | PRESSURE INDICATOR | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - |  | 214359C-6602-PID-0041-0002 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660P5234 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TT5126 | - | FRACTIONATOR OFF-GAS KNOCKOUT DRUM | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 100 | - | c | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5126 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 2 | - | NO | - | NI (NOT INSULATED) | - | - | 0 | °C | - | 100 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM536/P13 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-6"-P-2040.0-1BB1 | HC | OTHER | 6.33 | 8.5 | 40 | 180 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5126-SP
- | - | - | - | 1 | - | 1 | - | 660PI5235 | - | NATURAL GAS FROM OSBL - 660PT5235 | PRESSURE INDICATOR | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0041-0002 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660P5235 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | 660TT5211 | - | API PLAN 5001B | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -20 | 400 | - | °C | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5211 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM538/P19 | - | E10201 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PT5249 | - | API PLAN PUMP 660G0102 | PRESSURE TRANSMITTER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 30 | - | bar | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5249 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM534/P20 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PT5216 | - | API PLAN PUMP 660G0103 | PRESSURE TRANSMITTER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -1 | 35 | - | bar | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5216 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM534/P21 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 2 | - | 660PSV5261A | - | Debutanizer 660-C-0001 | RELIEF VALVE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5261A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-8"-P-12.1-B1F | OTHER | OTHER | - | 4.8 | - | 247 | - | - | - | - | IV | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PSV -5261A-SP
- | - | - | - | 1 | - | 2 | - | 660PSV5261B | - | Debutanizer 660-C-0001 | RELIEF VALVE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5261B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-8"-P-12.1-B1F | OTHER | OTHER | - | 4.8 | - | 247 | - | - | - | - | IV | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PSV -5261B-SP
- | - | - | - | 1 | - | 2 | - | 660PSV5261C | - | Debutanizer 660-C-0001 | RELIEF VALVE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5261C | C2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-8"-P-12.1-B1F | OTHER | OTHER | - | 4.8 | - | 247 | - | - | - | - | IV | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PSV -5261C-SP
- | - | - | - | 1 | - | 1 | - | 660PG5265 | - | API PLAN PUMP 660G5001B | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5265 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PG5267 | - | API PLAN PUMP 660G5001B | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5267 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PC5281 | - | FROM 660D0004 - 660PT5281 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660P5281 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660PT5281 | - | DEBUTANIZER RECEIVER | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 10 | - | bar Gage | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5281 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 3 | CI2 | P | LP | TV3 | STD RC INS 220 / FOLIO 21 | - | 0 | bar | Gage | 10 | bar | Gage | -1 | bar | Gage | 35 | bar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM535/P07 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-6"-P-2050.0-1BB1 | OTHER | OTHER | 3.8 | 5.5 | 40 | 160 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PT -5281-SP
- | - | CV01 | - | 3 | - | 1 | - | 660PV5281A | - | OFF GAS TO LPG RECOVERY (JET MODE) | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5281 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA004 | CI1/CI9/CI10 | P | LP | TV3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM535/P08 | - | E10201 | 660IADM516/02 | - | - | - | - | - | - | - | - | 660-6"-P-2050.0-1BB1 | OTHER | OTHER | 3.59 | 5.5 | 40 | 160 | - | - | - | - | III module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PV -5281A-SP
- | - | CV01 | - | 4 | - | 1 | - | 660PV5281B | - | OFF GAS TO LPG RECOVERY (DIESEL MODE) | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5281 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA004 | CI1/CI9/CI10 | P | LP | TV3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM535/P09 | - | E10201 | 660IADM516/03 | - | - | - | - | - | - | - | - | 660-2"-P-2050.0-1BB1 | OTHER | OTHER | 3.78 | 5.5 | 40 | 160 | - | - | - | - | III module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PV -5281B-SP
- | - | CV01 | - | 5 | - | 1 | - | 660PV5281C | - | OFF GAS TO FLARE | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5281 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA004 | CI1/CI9/CI10 | P | LP | TV3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM535/P10 | - | E10201 | 660IADM516/04 | - | - | - | - | - | - | - | - | 660-6"-P-2050.0-1BB1 | OTHER | OTHER | 3.59 | 5.5 | 40 | 160 | - | - | - | - | III module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PV -5281C-SP
- | - | - | - | 6 | - | 1 | - | 660PY5281 | - | FROM 660D0004 - 660PT5281 | SOFT CALCULATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660P5281 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 1 | - | 660PY5281A | - | FROM 660D0004 - 660PT5281 | SOFT CALCULATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660P5281 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PG5282 | - | DEBUTANIZER RECEIVER | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5282 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 2 FOLIO 7 | Cl6 | P | LP | TV3 | STD RC INS 220 / FOLIO 23 | - | - | - | - | - | - | - | -1 | bar | Gage | 5 | bar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2050.0-1BB1 | OTHER | OTHER | 3.8 | 5.5 | 40 | 160 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PG -5282-SP
- | - | - | - | 3 | - | 1 | - | 660TT5024 | - | KEROSENE STRIPPER REBOILER RETURN | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 350 | - | c | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5024 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 2 | - | NO | - | CC | - | - | 0 | °C | - | 350 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM530/P15 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-14"-P-2012.0-1BB3 | KERO | OTHER | 1.05 | 4.5 | 245 | 310 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5024-SP
- | - | - | - | 1 | - | 1 | - | 660PSV5288 | - | API PLAN PUMP 660G5002A | RELIEF VALVE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5288 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | - | - | - | PP | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | IV | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5025 | - | KEROSENE STRIPPER REBOILER INLET | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 300 | - | C | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5025 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 2 | - | NO | - | CC | - | - | 0 | °C | - | 300 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM530/P16 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-8"-P-2013.0-1BB3 | KERO | L | 1.11 | 4.6 | 217 | 280 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5025-SP
- | - | - | - | 1 | - | 1 | - | 660PSV5290 | - | API PLAN PUMP 660G5002B | RELIEF VALVE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5290 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | - | - | - | PP | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | IV | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PC5301A | - | TO 660F5001 - 660PT5301 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660P5301 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660PY5301A | - | TO 660F5001 - 660PT5301 | SOFT CALCULATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660P5301 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TT5022 | - | DIESEL PRODUCT TO BATTERY LIMIT | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 100 | - | °C | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5022 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 2 | - | NO | - | NI (NOT INSULATED) | - | - | 0 | °C | - | 100 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM531/P18 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-4"-P-2008.0-3BB1 | OTHER | L | 2.51 | 19 | 40 | 260 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5022-SP
- | - | CV01 | - | 4 | - | 1 | - | 660PV5301 | - | TO 660 F 5001 BURNERS | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5301 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA004 | CI1/CI9 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM538/P06 | - | E10201 | 660IADM514/05 | - | - | - | - | - | - | - | - | 660-4"-FG-2095.0-1KB2 | GN | OTHER | 2.75 | 3.5 | 41 | 75 | - | - | - | - | III module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PV -5301-SP
- | - | - | - | 5 | - | 1 | - | 660PAH5301B | - | TO 660F5001 - 660PT5301 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | High Alarm (2.5) | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660P5301 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660PAL5301A | - | TO 660F5001 - 660PT5301 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | Low Alarm (1.5) | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660P5301 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 1 | - | 660PC5301B | - | TO 660F5001 - 660PT5301 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660P5301 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 1 | - | 660PY5301B | - | TO 660F5001 - 660PT5301 | SOFT CALCULATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660P5301 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PI5302 | - | TO 660F5001 - 660PTS5302 | INDICATION | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660P5302 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660PTS5302 | - | NATURAL GAS TO 660 F 5001 BURNERS | PRESSURE REL | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | 0 | 4 | - | bar gage | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5302 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 3 | CI2 | NO | - | CC | - | - | 0 | bar | Gage | 4 | bar | Gage | -1 | bar | Gage | 35 | bar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS532/P01 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-4"-FG-2222.0-1KB2 | GN | OTHER | 2 | 3.5 | 41 | 75 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PTS -5302-SP
- | - | - | - | 3 | - | 1 | - | 660PSLL5302 | 660-PALL -5302 | TO 660F5001 - 660PTS5302 | ALARM | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - | - | - | Low low Alarm (0.08) | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5302 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660PSHH5302 | - | TO 660F5001 - 660PTS5302 | ALARM | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - | - | - | High High Alarm (2.10) | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5302 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660PAX5302 | - | TO 660F5001 - 660PTS5302 | ALARM | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5302 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PG5303 | - | NATURAL GAS TO 660 F 5001 BURNERS | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5303 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 2 FOLIO 6 | Cl2 | NO | - | CC | - | - | - | - | - | - | - | - | 0 | bar | Gage | 4 | bar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-4"-FG-2222.0-1KB2 | GN | OTHER | 2 | 3.5 | 41 | 75 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PG -5303-SP
- | - | - | - | 1 | - | 1 | - | 660PCV5304 | - | TO 660 F 5001 BURNERS | PRESSURE REGULATOR | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5304 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-4"-FG-2095.0-1KB2 | GN | OTHER | - | 3.5 | - | 75 | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PCV -5304-SP
- | - | - | - | 1 | - | 1 | - | 660PTS5305A | - | NATURAL GAS TO 660 F 5001 PILOTS | PRESSURE REL | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | 0 | 4 | - | bar gage | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5305 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 3 | CI2 | NO | - | CC | - | - | 0 | bar | Gage | 4 | bar | Gage | -1 | bar | Gage | 35 | bar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS532/P02 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-1 1/2"-FG-2223.0-1KB2 | GN | OTHER | 1.8 | 3.5 | 41 | 75 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PTS -5305A-SP
- | - | - | - | 2 | - | 1 | - | 660PTS5305B | - | NATURAL GAS TO 660 F 5001 PILOTS | PRESSURE REL | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | 0 | 4 | - | bar gage | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5305 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 3 | CI2 | NO | - | CC | - | - | 0 | bar | Gage | 4 | bar | Gage | -1 | bar | Gage | 35 | bar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS532/P03 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-1 1/2"-FG-2223.0-1KB2 | GN | OTHER | 1.8 | 3.5 | 41 | 75 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PTS -5305B-SP
- | - | - | - | 3 | - | 1 | - | 660PTS5305C | - | NATURAL GAS TO 660 F 5001 PILOTS | PRESSURE REL | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | 0 | 4 | - | bar gage | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5305 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 3 | CI2 | NO | - | CC | - | - | 0 | bar | Gage | 4 | bar | Gage | -1 | bar | Gage | 35 | bar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS538/P02 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-1 1/2"-FG-2223.0-1KB2 | GN | OTHER | 1.8 | 3.5 | 41 | 75 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PTS -5305C-SP
- | - | - | - | 4 | - | 1 | - | 660PI5305A | - | TO 660F5001 - 660PTS5305ABC | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660P5305 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660PI5305B | - | TO 660F5001 - 660PTS5305ABC | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660P5305 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660PI5305C | - | TO 660F5001 - 660PTS5305ABC | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660P5305 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 1 | - | 660PSHH5305A | - | TO 660F5001 - 660PTS5305ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | High Alarm (2.5) / High-High Alamr (3) | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660P5305 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 1 | - | 660PSHH5305B | - | TO 660F5001 - 660PTS5305ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | High Alarm (2.5) / High-High Alamr (3) | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660P5305 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 9 | - | 1 | - | 660PSHH5305C | - | TO 660F5001 - 660PTS5305ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | High Alarm (2.5) / High-High Alamr (3) | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660P5305 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 10 | - | 1 | - | 660PSLL5305A | - | TO 660F5001 - 660PTS5305ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | Low Alarm (1.5) / Low-Low Alamr (0.8) | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660P5305 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 11 | - | 1 | - | 660PSLL5305B | - | TO 660F5001 - 660PTS5305ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | Low Alarm (1.5) / Low-Low Alamr (0.8) | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660P5305 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 12 | - | 1 | - | 660PSLL5305C | - | TO 660F5001 - 660PTS5305ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | Low Alarm (1.5) / Low-Low Alamr (0.8) | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660P5305 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 13 | - | 1 | - | 660PAHH5305 | - | TO 660F5001 - 660PTS5305ABC | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | High High Alarm (1.5) | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5305 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 14 | - | 1 | - | 660PALL5305 | - | TO 660F5001 - 660PTS5305ABC | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | Low Low Alarm (1.5) | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5305 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 15 | - | 1 | - | 660PAX5305 | - | TO 660F5001 - 660PTS5305ABC | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5305 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 16 | - | 1 | - | 660PSH5305 | - | TO 660F5001 - 660PTS5305ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1C | SIS | DCS | - | - | - | 2.5 | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660P5305 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 17 | - | 1 | - | 660PSL5305 | - | TO 660F5001 - 660PTS5305ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1C | SIS | DCS | - | - | - | 1.5 | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660P5305 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 18 | - | 1 | - | 660PAH5305 | - | TO 660F5001 - 660PTS5305ABC | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | Low Alarm (1.5) | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5305 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 19 | - | 1 | - | 660PAL5305 | - | TO 660F5001 - 660PTS5305ABC | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | Low Alarm (0.8) | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5305 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PG5306 | - | NATURAL GAS TO 660 F 5001 PILOTS | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5306 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 2 FOLIO 6 | Cl2 | NO | - | CC | - | - | - | - | - | - | - | - | 0 | bar | Gage | 4 | bar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-1 1/2"-FG-2223.0-1KB2 | GN | OTHER | 1.8 | 3.5 | 41 | 75 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PG -5306-SP
- | - | - | - | 1 | - | 1 | - | 660PCV5307 | - | PILOT GAS TO 660 F 5001 | PRESSURE REGULATOR | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5307 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-1 1/2"-FG-2095.1-1KB2 | GN | OTHER | 2.76 | 3.5 | 41 | 75 | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PCV -5307-SP
- | - | - | - | 1 | - | 1 | - | 660PC5308A | - | TO 660 F 5001 - 660PT5308 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660P5308 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660PC5308B | - | TO 660 F 5001 - 660PT5308 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660P5308 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TT5021 | - | PRODUCT FRACTIONATOR REBOILER | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 400 | - | c | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5021 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 2 | - | NO | - | CC | - | - | 0 | °C | - | 400 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM532/P08 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-6"-P-2010.0-3BB3 | OTHER | OTHER | 1.7 | 5.2 | 361 | 390 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5021-SP
- | - | - | - | 3 | - | 1 | - | 660TT5050 | - | PRODUCT FRACTIONATOR REBOILER | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 750 | - | °C | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | Alarm H: 535 | - | - | - | 3 | 660T5050 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | CI3 | NO | - | NI (NOT INSULATED) | N | - | 0 | °C | - | 750 | °C | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM532/P09 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660PV5316 | - | TO 660 F 5001 | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5308 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/Pag4 | CI1/CI9 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660UYS5308 | - | TO 660 F 5001 | AIR SOLENOID SPRING | - | - | SOLENOID ONLY | - | - | L | ST1D | BPCS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660P5308 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS501/C01-C02 | - | E10207 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 1 | - | 660UZSH5308 | - | TO 660 F 5001 | LIMIT SWITCH | - | - | INDUCTIVE | - | - | L | ST1D | BPCS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660P5308 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS504/P03 | - | With UZSL | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 4 | - | 1 | - | 660UZSH5377A | 660-UZSH -5377 | FUEL GAS TO F 5001 BURNER A | LIMIT SWITCH | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5377A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS504/P04 | - | With UZSL | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PT5395 | - | COMBUSTION AIR FAN DISCHARGE | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 50 | - | mbar Gage | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5395 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 3 | CI2 | NO | - | NI (NOT INSULATED) | - | - | 0 | mbar | Gage | 50 | mbar | Gage | -50 | mbar | Gage | 50 | mbar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM537/P03 | - | E10201 | - | - | - | - | - | - | - | - | - | DUCTS | OTHER | OTHER | 0.02 | 2.5 | 15 | 61 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PG -5395-SP
- | - | - | - | 2 | - | 1 | - | 660PAH5309 | - | 660K5001 FLUE GAS PRESSURE - 660PT5309 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | High Alarm (0.20) | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5309 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660PI5309 | - | 660K5001 FLUE GAS PRESSURE - 660PT5309 | PRESSURE INDICATOR | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5309 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5051 | - | PRODUCT FRACTIONATOR REBOILER | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 750 | - | °C | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | Alarm H: 535 | - | - | - | 3 | 660T5051 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | CI3 | NO | - | NI (NOT INSULATED) | N | - | 0 | °C | - | 750 | °C | - | -260 | °C | - | 1260 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM532/P10 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660PI5310 | - | 660K5001 FLUE GAS PRESSURE - 660PT5310 | PRESSURE INDICATOR | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5310 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PG5312B | - | 660 F 5001 BURNER N°2 | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5312 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 2 FOLIO 23 | CI2 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | -1 | bar | Gage | 1.5 | bar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | FG | OTHER | 0 | 2.5 | 845 | 1100 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PG -5312-SP
- | - | - | - | 2 | - | 1 | - | 660PG5312A | - | 660 F 5001 BURNER N°1 | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5312 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 2 FOLIO 23 | CI2 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | -1 | bar | Gage | 1.5 | bar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | FG | OTHER | 0 | 2.5 | 845 | 1100 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-PG -5312A-SP
- | - | - | - | 3 | - | 1 | - | 660PG5312D | - | 660 F 5001 BURNER N°4 | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5312 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 2 FOLIO 23 | CI2 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | -1 | bar | Gage | 1.5 | bar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | FG | OTHER | 0 | 2.5 | 845 | 1100 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-PG -5312D-SP
- | - | - | - | 1 | - | 1 | - | 660PG5312C | - | 660 F 5001 BURNER N°3 | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5312C | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 2 FOLIO 23 | CI2 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | -1 | bar | Gage | 1.5 | bar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | FG | OTHER | 0 | 2.5 | 845 | 1100 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-PG -5312C-SP
- | - | - | - | 1 | - | 1 | - | 660PG5313 | - | HOLD | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5313 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PT5396 | - | COMBUSTION AIR FAN | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 15 | - | mbar Gage | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5396 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 2 | CI2 | NO | - | NI (NOT INSULATED) | - | - | -15 | mbar | Gage | 15 | mbar | Gage | -50 | mbar | Gage | 50 | mbar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM537/P04 | - | E10201 | - | - | - | - | - | - | - | - | - | DUCTS | OTHER | OTHER | -0.01 | 2.5 | 15 | 61 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PG -5396-SP
- | - | - | - | 2 | - | 1 | - | 660PI5314 | - | COMBUSTION AIR TO PRODUCT FRAC REBOILER-660PT5314 | PRESSURE INDICATOR | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5314 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5052 | - | PRODUCT FRACTIONATOR REBOILER | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 750 | - | °C | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | Alarm H: 535 | - | - | - | 3 | 660T5052 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | CI3 | NO | - | NI (NOT INSULATED) | N | - | 0 | °C | - | 750 | °C | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM532/P11 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660PI5315 | - | PRODUCT FRACTIONATOR REBOILER - 660PT5315 | PRESSURE INDICATOR | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5315 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PTS5316A | - | AIR TO 660 F 5001 | PRESSURE REL | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5316 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660PTS5316B | - | AIR TO 660 F 5001 | PRESSURE REL | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5316 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660PTS5316C | - | AIR TO 660 F 5001 | PRESSURE REL | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5316 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660PALL5316 | - | AIR TO 660 F 5001 | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5316 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660PI5316A | - | AIR TO 660 F 5001 | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660P5316 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660PI5316B | - | AIR TO 660 F 5001 | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660P5316 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 1 | - | 660PI5316C | - | AIR TO 660 F 5001 | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660P5316 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PG5317 | - | HOLD | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5317 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660PDG5317 | - | 660K5001 FLUE GAS PRESSURE | PRESSURE DP GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5317 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2x STD-RC-INS-412 / PART 2 FOLIO 23 | CI6 | NO | - | NI (NOT INSULATED) | Capillary 214359C-1000-STD-1576-0002-Pg4 | - | - | - | - | - | - | - | 0 | mbar | Gage | 25 | mbar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | FG | OTHER | 0 | 2.5 | 371 | 430 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PDG -5317-SP
- | - | - | - | 1 | - | 1 | - | 660PG5320 | - | HOLD | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0221 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5320 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 2 FOLIO 21 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PDG5321 | - | FUEL GAS BASKET STRAINER | PRESSURE DP GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0221 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5321 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | CI2 | - | - | CC | - | - | - | - | - | - | - | - | 0 | mbar | Gage | 100 | mbar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-4"-FG-2094.0-1BB1 | - | - | - | - | - | - | - | - | - | - | 1) PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PDT5322 | - | FUEL GAS BASKET STRAINER | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0221 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5322 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-411 / PART 3 FOLIO 3 | CI2 | - | - | CC | - | - | 0 | bar | - | 0.1 | bar | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-4"-FG-2094.0-1BB1 | - | - | - | - | - | - | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660PDI5322 | 660-PDI -5321 | 660 D 5012A/B | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0221 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660P5322 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | 660PTS5332 | - | FUEL GAS TO F 5001 BURNERS | PRESSURE REL | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | 0 | 4 | - | bar gage | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5332 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 2 | CI2 | NO | - | CC | - | - | 0 | bar | Gage | 4 | bar | - | -1 | bar | Gage | 35 | bar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS538/P03 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-1 1/2"-FG-2095.1-1KB2 | GN | OTHER | 2.76 | 3.5 | 41 | 75 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PT -5332-SP
- | - | - | - | 1 | - | 1 | - | 660PI5332 | - | FUEL GAS TO F 5001 BURNERS - 660PTS5332 | INDICATION | - | - | - | N | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660P5332 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | 660PTS5334 | - | FUEL GAS TO F 5001 BURNERS | PRESSURE REL | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | 0 | 4 | - | bar gage | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5334 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 2 | CI2 | NO | - | CC | - | - | 0 | bar | Gage | 4 | bar | Gage | -1 | bar | Gage | 35 | bar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS532/P04 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-4"-FG-2095.0-1KB2 | GN | OTHER | 2.75 | 3.5 | 41 | 75 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PT -5334-SP
- | - | - | - | 1 | - | 1 | - | 660PI5334 | - | FUEL GAS TO F 5001 BURNERS - 660PTS5334 | INDICATION | - | - | - | N | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660P5334 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PTS5335 | - | 660K5001 FLUE GAS PRESSURE | PRESSURE REL | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | -0.5 | 0.5 | - | mbar gage | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5335 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 3 | HOLD | NO | - | CC | - | - | -0.5 | mbar | Gage | 0.5 | mbar | Gage | -50 | mbar | - | 50 | mbar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS538/P04 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | FG | OTHER | 0 | 2.5 | 374 | 1100 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PTS -5335-SP
- | - | - | - | 2 | - | 1 | - | 660PAH5335 | - | 660K5001 FLUE GAS PRESSURE | ALARM | - | - | - | N | - | CRD | SdC | SIS | S-PLC | - | - | - | High Alarm (0.20) | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5335 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660PI5335 | - | 660K5001 FLUE GAS PRESSURE | PRESSURE INDICATOR | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5335 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660PAX5335 | - | 660K5001 FLUE GAS PRESSURE - 660PTS5335 | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5335 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660PAHH5335 | - | 660K5001 FLUE GAS PRESSURE - 660PTS5335 | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | High High Alarm (2.50) | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5335 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PG5370 | - | BURNER NATURAL GAS 660 F 5001 | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5370 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 2 FOLIO 6 | Cl6 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | 0 | bar | Gage | 4 | bar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-2"-FG-2222.0-1KB2 | GN | OTHER | 2 | 3.5 | 41 | 75 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PG -5370-SP
- | - | - | - | 1 | - | 1 | - | 660PG5372 | - | BURNER NATURAL GAS 660 F 5001 | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5372 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 2 FOLIO 6 | Cl6 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | 0 | bar | Gage | 4 | bar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-2"-FG-2222.0-1KB2 | GN | OTHER | 1.8 | 3.5 | 41 | 75 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PG -5372-SP
- | - | - | - | 1 | - | 1 | - | 660PG5374 | - | BURNER NATURAL GAS 660 F 5001 | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5374 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 2 FOLIO 6 | Cl6 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | 0 | bar | Gage | 4 | bar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-2"-FG-2222.0-1KB2 | GN | OTHER | 2 | 3.5 | 41 | 75 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PG -5374-SP
- | - | - | - | 1 | - | 1 | - | 660PG5376 | - | BURNER NATURAL GAS 660 F 5001 | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5376 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 2 FOLIO 6 | Cl6 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | 0 | bar | Gage | 4 | bar | Gage | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-2"-FG-2222.0-1KB2 | GN | OTHER | 1.8 | 3.5 | 41 | 75 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PG -5376-SP
- | - | CV01 | - | 4 | - | 1 | - | 660PV5181 | 660PV5182B | OFF GAS FROM 660 D 5001 TO FLARE | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5181 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA004 | CI1/CI9/CI10 | P | LP | TV3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM533/P05 | - | E10201 | 660IADM518/03 | - | - | - | - | - | - | - | - | 660-8"-P-2028.1-1BB1 | OTHER | OTHER | 0.34 | 4 | 40 | 160 | - | - | - | - | III module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PV -5181-SP
- | - | CV01 | - | 1 | - | 1 | - | 660PV5182 | 660PV5182A | OFFGAS COMPRESSOR SPILLBACK | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5182 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA004 | CI1/CI9 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM533/P06 | - | E10201 | 660IADM518/04 | - | - | - | - | - | - | - | - | 660-6"-P-2037.0-1BB1 | OTHER | OTHER | 0 | 8 | - | 180 | - | - | - | - | III module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PV -5182 (2 cases)
- | - | - | - | 1 | - | 1 | - | 660PG5393 | - | HOLD | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5393 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5053 | - | PRODUCT FRACTIONATOR REBOILER | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 750 | - | °C | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | Alarm H: 535 | - | - | - | 3 | 660T5053 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | CI3 | NO | - | NI (NOT INSULATED) | N | - | 0 | °C | - | 750 | °C | - | -260 | °C | - | 1260 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM532/P12 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660PI5394 | - | PRODUCT FRACTIONATOR REBOILER - 660PT5394 | PRESSURE INDICATOR | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5394 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PT5397 | - | COMBUSTION AIR FAN | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5397 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 3 | CI2 | NO | - | NI (NOT INSULATED) | - | - | -1 | mbar | Gage | 1 | mbar | Gage | -50 | mbar | Gage | 50 | mbar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM537/P05 | - | E10201 | - | - | - | - | - | - | - | - | - | DUCTS | FG | OTHER | 0 | 2.5 | 120 | 196 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PT -5397-SP
- | - | - | - | 2 | - | 1 | - | 660PI5395 | - | COMBUSTION AIR FAN DISCHARGE - 660PT5395 | PRESSURE INDICATOR | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5395 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PT5398 | - | INDUCED DRAFT FLUE GAS FAN SUCTION | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 30 | - | mbar Gage | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5398 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 2 | CI2 | NO | - | NI (NOT INSULATED) | - | - | -30 | mbar | Gage | 30 | mbar | Gage | -50 | mbar | Gage | 50 | mbar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM537/P06 | - | E10201 | - | - | - | - | - | - | - | - | - | DUCTS | FG | OTHER | -0.01 | 2.5 | 120 | 196 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PG -5398-SP
- | - | - | - | 2 | - | 1 | - | 660PI5396 | - | COMBUSTION AIR FAN - 660PT5396 | PRESSURE INDICATOR | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5396 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5303 | - | COMBUSTION AIR PREHEATER - AIR OUTLET | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 100 | - | c | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5303 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-441 / PART 1 FOLIO 9 | - | NO | - | NI (NOT INSULATED) | - | - | 0 | °C | - | 100 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM537/P07 | - | E10201 | - | - | - | - | - | - | - | - | - | DUCTS | OTHER | OTHER | 0.03 | 2.5 | 15 | 61 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5303-SP
- | - | - | - | 2 | - | 1 | - | 660PI5397 | - | COMBUSTION AIR FAN - 660PT5397 | PRESSURE INDICATOR | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | -1 | 1 | - | mbar Gage | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5397 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5304 | - | PRODUCT FRACTIONATOR REBOILER | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 450 | - | c | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5304 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-441 / PART 1 FOLIO 9 | - | NO | - | NI (NOT INSULATED) | - | - | 0 | °C | - | 450 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM537/P08 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | OTHER | OTHER | 0 | 2.5 | 371 | 450 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5304-SP
- | - | - | - | 2 | - | 1 | - | 660PI5398 | - | INDUCED DRAFT FLUE GAS FAN SUCTION - 660PT5398 | PRESSURE INDICATOR | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5398 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660TT5087 | - | PRODUCT FRACTIONATOR REBOILER | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 400 | - | c | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5087 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 2 | - | NO | - | CC | - | - | 0 | °C | - | 400 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM532/P13 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-6"-P-2010.1-3BB3 | OTHER | OTHER | 1.7 | 5.2 | 361 | 390 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5087-SP
- | - | - | - | 2 | - | 1 | - | 660PI5399 | - | PRODUCT FRACTIONATOR REBOILER - 660PT5399 | PRESSURE INDICATOR | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5399 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PT5415 | - | API PLAN PUMP 660G0003 | PRESSURE TRANSMITTER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -1 | 35 | - | bar | 214359C-6602-PID-0021-0218 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5415 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM534/P22 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PG5501 | 660PI5133 | FRACTIONATOR OFF-GAS COMPRESSOR SUCTION | PRESSURE GAUGE | - | - | - | - | - | LP | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5501 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 2 FOLIO 8 | Cl6 | P | LP | TV3 | STD RC INS 220 / FOLIO 23 | - | - | - | - | - | - | - | -1 | bar | Gage | - | bar | Gage | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-14"-P-2028.0-1BB1 | OTHER | OTHER | 0.4 | 4 | 40 | 160 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PG -5501-SP
- | - | - | - | 1 | - | 1 | - | 660PG5502 | 660PT5134 | FRACTIONATOR OFF-GAS COMPRESSOR DISCHARGE | PRESSURE GAUGE | - | - | - | - | - | LP | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5502 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-412 / PART 2 FOLIO 8 | Cl6 | NO | - | PP | - | - | - | - | - | - | - | - | -1 | bar | Gage | 9 | bar | Gage | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2035.0-1BB1 | OTHER | OTHER | 6.7 | 8.5 | 179 | 200 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-PG -5502-SP
- | - | - | - | 1 | - | 1 | - | 660PG5550 | - | 660 K 5001 COMPRESSOR | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5550 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | bar | - | 10 | bar | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PG5551 | - | 660 K 5001 COMPRESSOR | PRESSURE GAUGE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5551 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | bar | - | 10 | bar | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PCV5555 | - | 660 K 5001 COMPRESSOR | PRESSURE REGULATOR | - | - | - | - | - | L | - | - | - | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5555 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PCV5556 | - | 660 K 5001 COMPRESSOR | PRESSURE REGULATOR | - | - | - | - | - | L | - | - | - | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5556 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PCV5557 | - | 660 K 5001 COMPRESSOR | PRESSURE REGULATOR | - | - | - | - | - | L | - | - | - | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5557 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TT5555 | - | 660 K 5001 COMPRESSOR | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | -20 | 140 | High Alaam (65 °C) Law Alaam (10 °C) | °C | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5555 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | CI6 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | -20 | °C | - | 140 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM515/P03 | - | - | - | - | - | - | - | - | - | - | - | 660-4"-P-2008.0-3BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660PDI5558 | - | 660 K 5001 COMPRESSOR | DIFFERENTIAL PRESSURE INDICATOR | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | Alarm H: 1 | - | - | - | 5 | 660P5558 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660PDAL5558 | - | 660 K 5001 COMPRESSOR | LOW DIFF. PRESSURE ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5558 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PDT5558 | - | 660 K 5001 COMPRESSOR | DIFFERENTIAL PRESSURE TRANSMITTER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 25 | 5000 | High Alarm (1.0 bar) | mbar | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5558 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | - | - | - | - | - | - | - | - | - | - | - | - | 25 | mbar | - | 5000 | mbar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM515/P04 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660PDI5559 | - | 660 K 5001 COMPRESSOR | DIFFERENTIAL PRESSURE INDICATOR | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660P5559 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PDAL5560A | - | 660 K 5001 COMPRESSOR | LOW DIFF. PRESSURE ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | Low Alaram (2.5 bar) Low Low Alarm(2.0 bar) | mbar | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5560 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660PDAL5560B | - | 660 K 5001 COMPRESSOR | LOW DIFF. PRESSURE ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | Low Alaram (2.5 bar) Low Low Alarm(2.0 bar) | mbar | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5560 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660PDAL5560C | - | 660 K 5001 COMPRESSOR | LOW DIFF. PRESSURE ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | Low Alaram (2.5 bar) Low Low Alarm(2.0 bar) | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5560 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660PDALL5560 | - | 660 K 5001 COMPRESSOR | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5560 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660PDI5560A | - | 660 K 5001 COMPRESSOR | DIFFERENTIAL PRESSURE INDICATOR | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | Alarm L: 2.5 bar Alarm LL: 2 bar | - | - | - | 5 | 660P5560 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660PDI5560B | - | 660 K 5001 COMPRESSOR | DIFFERENTIAL PRESSURE INDICATOR | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | Alarm L: 2.5 bar Alarm LL: 2 bar | - | - | - | 5 | 660P5560 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 1 | - | 660PDI5560C | - | 660 K 5001 COMPRESSOR | DIFFERENTIAL PRESSURE INDICATOR | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | Alarm L: 2.5 bar Alarm LL: 2 bar | - | - | - | 5 | 660P5560 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 1 | - | 660PDTS5560A | - | 660 K 5001 COMPRESSOR | PRESSURE DP | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | 25 | 5000 | - | mbar | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5560 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 25 | mbar | - | 5000 | mbar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS520/P01 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 9 | - | 1 | - | 660PDTS5560B | - | 660 K 5001 COMPRESSOR | PRESSURE DP | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | 25 | 5000 | - | mbar | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5560 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 25 | mbar | - | 5000 | mbar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS520/P02 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 10 | - | 1 | - | 660PDTS5560C | - | 660 K 5001 COMPRESSOR | PRESSURE DP | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | 25 | 5000 | - | mbar | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5560 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 25 | mbar | - | 5000 | mbar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS520/P03 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PI5561 | - | 660 K 5001 COMPRESSOR | PRESSURE INDICATOR | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | Alarm L: 4 | - | - | - | 5 | 660P5561 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PDT5559 | - | 660 K 5001 COMPRESSOR | DIFFERENTIAL PRESSURE TRANSMITTER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 25 | 5000 | - | mbar | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5559 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | - | - | - | - | - | - | - | - | - | - | - | - | 25 | mbar | - | 5000 | mbar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM515/P05 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660PAL5561 | - | 660 K 5001 COMPRESSOR | LOW-PRESSURE ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | Low Alarm (4) | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5561 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PAL5562A | - | 660 K 5001 COMPRESSOR | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | High Alaam (4 barg) Low Alaram (1.5 barg) Low Low Alarm(1.0 barg) | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5562 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660PAL5562B | - | 660 K 5001 COMPRESSOR | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | High Alaam (4 barg) Low Alaram (1.5 barg) Low Low Alarm(1.0 barg) | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5562 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660PAL5562C | - | 660 K 5001 COMPRESSOR | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | High Alaam (4 barg) Low Alaram (1.5 barg) Low Low Alarm(1.0 barg) | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5562 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660PALL5562 | - | 660 K 5001 COMPRESSOR | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | Low Low Alarm(2.0 barg) | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660P5562 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660PI5562A | - | 660 K 5001 COMPRESSOR | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | Alarm H: 4 Alarm L: 1.5 Alarm LL: 1 | - | - | - | 5 | 660P5562 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660PI5562B | - | 660 K 5001 COMPRESSOR | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | Alarm H: 4 Alarm L: 1.5 Alarm LL: 1 | - | - | - | 5 | 660P5562 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 1 | - | 660PI5562C | - | 660 K 5001 COMPRESSOR | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | Alarm H: 4 Alarm L: 1.5 Alarm LL: 1 | - | - | - | 5 | 660P5562 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 1 | - | 660PTS5562A | - | 660 K 5001 COMPRESSOR | PRESSURE REL | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | 0.175 | 35 | - | bar | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5562 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | - | - | - | - | - | - | - | - | - | - | - | - | 0.18 | bar | - | 35 | bar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS520/P04 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 9 | - | 1 | - | 660PTS5562B | - | 660 K 5001 COMPRESSOR | PRESSURE REL | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | 0.175 | 35 | - | bar | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5562 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | - | - | - | - | - | - | - | - | - | - | - | - | 0.18 | bar | - | 35 | bar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS520/P05 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 10 | - | 1 | - | 660PTS5562C | - | 660 K 5001 COMPRESSOR | PRESSURE REL | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | 0.175 | 35 | - | bar | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5562 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | - | - | - | - | - | - | - | - | - | - | - | - | 0.18 | bar | - | 35 | bar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS520/P06 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PT5565 | - | HOLD | PRESSURE TRANSMITTER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - |  | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5565 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Gage | - | - | - | - | - | Gage | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-4"-P-2008.0-3BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PT5566 | - | HOLD | PRESSURE TRANSMITTER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - |  | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5566 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Gage | - | - | - | - | - | Gage | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-4"-P-2026.0-3BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660PT5561 | - | 660 K 5001 COMPRESSOR | PRESSURE TRANSMITTER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0.175 | 35 |  | barg | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5561 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | - | - | - | - | - | - | - | - | - | - | - | - | 0.18 | bar | - | 35 | bar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM515/P06 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TT0017 | - | DEBUTANIZER | TEMPERATURE CONV | - | - | IN ITR | N | - | ITR | ST7 | BPCS | DCS | - | 0 | 200 | - | c | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T0017 | U | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 4 | CI6 | NO | - | NI (NOT INSULATED) | - | - | 0 | °C | - | 100 | °C | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-10"-P-2044.0-1BB1 | HC | L-G | 4.1 | - | 53 | - | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | II | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TW0017 | - | TO 660 C 0001 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T0017 | R1D2 | NEW_LINE/EQUIP | - | - | - | - | TIP-660-5901-I | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-10"-P-2044.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-TW -0017-SP
- | - | - | - | 3 | - | 1 | - | 660TE0017 | - | TO 660 C 0001 | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T0017 | R1D2 | NEW_LINE/EQUIP | - | - | - | - | TIP-660-5901-I | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | 0 | °C | - | 200 | °C | - | -40 | °C | - | 750 | °C | - | - | - | - | - | - | AI30 | INT | - | - | - | - | - | - | - | - | - | - | 66BR1P/3, 55-56 | - | 01 JC 10 EGFA BLACK | - | - | - | - | - | JB info by OSBL | - | - | - | 660-10"-P-2044.0-1BB1 | HC | OTHER | 3.8 | 4.8 | 53 | 160 | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-TE -0017-SP
- | - | - | - | 4 | - | 1 | - | 660TI0017 | - | FROM 660 G 5003A/B | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T0017 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TG0024 | - | DEBUTANIZER RECEIVER | THERMOMETER | - | - | - | N | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T0024 | R1D2 | - | - | - | - | - | TIP-660-5903-I | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 4 | Cl1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | 0 | °C | - | 120 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2060.0-1BB1 | HC | OTHER | 3.8 | 5.5 | 40 | 120 | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TG -0024-SP
- | - | - | - | 2 | - | 1 | - | 660TW0024 | - | DEBUTANIZER RECEIVER | THERMOWELL | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T0024 | R1D2 | - | - | - | - | - | TIP-660-5903-I | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2060.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-TW -0024-SP
- | - | - | - | 1 | - | 1 | - | 660TW0027 | - | DEBUTANIZER BOTTOM COOLER BUNDLE OUTLET | THERMOWELL | - | - | - | N | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T0027 | U | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE0028 | - | DEBUTANIZER BOTTOM COOLER BUNDLE OUTLET | THERMOCOUPLE | - | - | - | N | - | L | ST7 | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T0028 | U | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI6 | NO | - | NI (NOT INSULATED) | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI31 | INT | NR | - | - | - | - | - | - | - | - | - | 66BR1P/3, 19-20 | - | - | - | - | - | - | - | JB info by OSBL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI0028 | - | TT0028 SORTIE E0104 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T0028 | U | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TW0028 | - | DEBUTANIZER BOTTOM COOLER BUNDLE OUTLET | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T0028 | U | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI6 | - | - | - | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE0030 | - | DEBUTANIZER BOTTOM COOLER INLET | THERMOCOUPLE | - | - | - | N | - | L | ST7 | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T0030 | U | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI6 | NO | - | NI (NOT INSULATED) | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI31 | INT | NR | - | - | - | - | - | - | - | - | - | 660BP06, 09-10 | - | - | - | - | - | - | - | JB info by OSBL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI0030 | - | TT0030 SORTIE E0005E/F -> E0004A | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T0030 | U | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TW0030 | - | DEBUTANIZER BOTTOM COOLER INLET | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T0030 | U | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI6 | NO | - | NI (NOT INSULATED) | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TT0085 | - | DEBUTANIZER BOTTOM COOLER OUTLET | TEMPERATURE CONV | - | - | IN ITR | N | - | ITR | ST7 | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T0085 | U | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI6 | NO | - | NI (NOT INSULATED) | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TIC0085 | - | TT0085 AERO EM0004/0104 | TEMPERATURE INDICATING CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660T0085 | U | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TE0085 | - | DEBUTANIZER BOTTOM COOLER OUTLET | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T0085 | U | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI6 | - | - | - | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 66BR1P/3, 22-23 | - | - | - | - | - | - | - | JB info by OSBL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TW0085 | - | DEBUTANIZER BOTTOM COOLER OUTLET | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T0085 | U | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI6 | - | - | - | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TT0087 | - | DEBUTANIZER | TEMPERATURE CONV | - | - | - | N | - | L | ST1C | BPCS | DCS | - | 0 | 200 | - | c | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T0087 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 4 | CI6 | NO | - | NI (NOT INSULATED) | - | - | 0 | °C | - | 100 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-10"-P-2044.0-1BB1 | - | - | - | - | - | - | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TW0087 | - | TO 660 C 0001 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T0087 | R1D2 | NEW_LINE/EQUIP | - | - | - | - | TIP-660-5902-I | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-10"-P-2044.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-TW -0087-SP
- | - | - | - | 3 | - | 1 | - | 660TE0087 | - | FO 660 C 0001 | THERMOCOUPLE | - | - | LLMUX | N | - | L | ST7 | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T0087 | R1D2 | NEW_LINE/EQUIP | - | - | - | - | TIP-660-5902-I | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | 0 | °C | - | 200 | °C | - | -40 | °C | - | 750 | °C | - | - | - | - | - | - | AI30 | INT | NR | - | - | - | - | - | - | - | - | - | 66BR1P/3, 25-26 | - | 01 JC 10 EGFA BLACK | - | - | - | - | - | - | - | - | - | 660-10"-P-2044.0-1BB1 | HC | OTHER | 3.8 | 4.8 | 53 | 160 | - | - | - | - | - | - | - | - | - | ATEX | 2 | II | T6 | - | - | - | - | - | - | - | 660-TE -0087-SP
- | - | - | - | 4 | - | 1 | - | 660TI0087 | - | FROM 660 G 5003A/B | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T0087 | M | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TT0088 | - | DEBUTANIZER | TEMPERATURE CONV | - | - | - | N | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T0088 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI6 | NO | - | NI (NOT INSULATED) | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TW0088 | - | DEBUTANIZER | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T0088 | U | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI6 | - | - | - | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TE0088 | - | DEBUTANIZER | THERMOCOUPLE | - | - | LLMUX | N | - | L | ST7 | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T0088 | U | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI6 | - | - | - | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI31 | INT | - | - | - | - | - | - | - | - | - | - | 66BR1P/3, 28-29 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TAL0088 | - | TO 660E5008 - 660TT0088 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660T0088 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE0089 | - | DEBUTANIZER BOTTOM COOLER | THERMOCOUPLE | - | - | LLMUX | N | - | L | ST7 | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T0089 | U | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI6 | NO | - | NI (NOT INSULATED) | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI31 | INT | NR | - | - | - | - | - | - | - | - | - | 66BR1P/3, 31-32 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI0089 | - | TT0089 G.O -> STOCK | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T0089 | U | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TAH0089 | - | TT0089 G.O -> STOCK | HIGH TEMPERATURE ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T0089 | U | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TAL0089 | - | TT0089 G.O -> STOCK | LOW-TEMPERATURE ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T0089 | U | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660TW0089 | - | DEBUTANIZER BOTTOM COOLER | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T0089 | U | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI6 | - | - | - | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TT0090 | - | HOLD | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T0090 | D1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD RC INS 440_PART 3_FOLIO 4 | CI6 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5044 | - | PRODUCT FRACTIONATOR TRAY #61 | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 400 | - | C | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5044 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-441 / PART 1 FOLIO 9 | - | NO | - | NI (NOT INSULATED) | - | - | 0 | °C | - | 400 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM538/P07 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | HC | OTHER | 0.86 | 3.5 | 301 | 390 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5044-SP
- | - | - | - | 1 | - | 1 | - | 660TAH5020 | - | FROM 660F5001 - 660TT5020 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | Alarm High (383) | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5020 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TE5020 | - | FROM 660 F 5001 | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5020 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-20"-P-2010.0-3BB3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TI5020 | - | FROM 660F5001 - 660TT5020 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5020 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TT5088 | - | PRODUCT FRACTIONATOR REBOILER | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 400 | - | c | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5088 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-441 / PART 1 FOLIO 9 | - | NO | - | NI (NOT INSULATED) | - | - | 0 | °C | - | 400 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM532/P14 | - | E10201 | - | - | - | - | - | - | - | - | - | DUCTS | HC | OTHER | 1.97 | 10 | 364 | 400 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5088-SP
- | - | - | - | 5 | - | 1 | - | 660TW5020 | - | FROM 660 F 5001 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5020 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-20"-P-2010.0-3BB3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TAH5021 | - | FROM 660F5001 - 660TT5021 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | Alarm High (383) | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5021 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TE5021 | - | FROM 660 F 5001 | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5021 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2010.0-3BB3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TI5021 | - | FROM 660F5001 - 660TT5021 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5021 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TT5089 | - | PRODUCT FRACTIONATOR REBOILER | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 400 | - | c | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5089 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-441 / PART 1 FOLIO 9 | - | NO | - | NI (NOT INSULATED) | - | - | 0 | °C | - | 400 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM532/P15 | - | E10201 | - | - | - | - | - | - | - | - | - | DUCTS | HC | OTHER | 1.97 | 10 | 364 | 400 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5089-SP
- | - | - | - | 5 | - | 1 | - | 660TW5021 | - | FROM 660 F 5001 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5021 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2010.0-3BB3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TAH5022 | - | BIODIESEL TO TANK FARM - 660TT5022 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | 45 | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5022 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TE5022 | - | BIODIESEL TO TANK FARM | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5022 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-4"-P-2008.0-3BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TI5022 | - | BIODIESEL TO TANK FARM - 660TT5022 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5022 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5041 | - | PRODUCT FRACTIONATOR | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 150 | - | C | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5041 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 2 | - | NO | - | PP | - | - | 0 | °C | - | 150 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM531/P19 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-24"-P-2002.0-1BB1 | OTHER | OTHER | 0.76 | 3.5 | 109 | 145 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5041-SP
- | - | - | - | 5 | - | 1 | - | 660TW5022 | - | BIODIESEL TO TANK FARM | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5022 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-4"-P-2008.0-3BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5023 | - | FROM 660 C 5002 | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5023 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-8"-P-2011.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5023 | - | FROM 660C5002 - 660TT5023 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5023 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TT5122 | - | KEROSENE PRODUCT RUNDOWN | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 250 | - | c | 214359C-6602-PID-0021-0209 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5122 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 2 | - | NO | - | CC | - | - | 0 | °C | - | 250 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM530/P17 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-4"-P-2021.0-3BB1 | KERO | L | 4.81 | 19 | 199 | 250 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5122-SP
- | - | - | - | 4 | - | 1 | - | 660TW5023 | - | FROM 660 C 5002 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5023 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-8"-P-2011.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5024 | - | TO 660 C 5002 | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5024 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-14"-P-2012.0-1BB3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5024 | - | TO 660C5002 - 660TT5024 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5024 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | 660TT5218 | - | API PLAN 5001B | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -20 | 400 | - | °C | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5218 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM538/P18 | - | E10201 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TW5024 | - | TO 660 C 5002 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5024 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-14"-P-2012.0-1BB3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660TAL5024 | - | TO 660C5002 - 660TT5024 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | Low Alarm (230) | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5024 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5025 | - | TO 660 E 5005 | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5025 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-8"-P-2013.0-1BB3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5025 | - | TO 660E5005 - 660TT5025 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5025 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5221 | - | DEBUTANIZER RECEIVER | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 100 | - | c | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5221 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 2 | - | NO | - | NI (NOT INSULATED) | - | - | 0 | °C | - | 100 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM535/P11 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-6"-P-2060.0-1BB1 | HC | L | 3.8 | 5.5 | 40 | 120 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5221-SP
- | - | - | - | 4 | - | 1 | - | 660TW5025 | - | TO 660 E 5005 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5025 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-8"-P-2013.0-1BB3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TW5026 | 660TW0026 | DEBUTANIZER BOTTOM COOLER BUNDLE INLET | THERMOWELL | - | - | - | N | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5026 | U | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TW5027 | 660TW0025 | DEBUTANIZER BOTTON COOLER BUNDLE INLET | THERMOWELL | - | - | - | N | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5027 | U | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5041 | - | FROM 660 C 5001 | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5041 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | PP | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-24"-P-2002.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5041 | - | FROM 660C5001 - 660TT5041 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5041 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5042 | - | PRODUCT FRACTIONATOR TRAY #65 | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 400 | - | C | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5042 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-441 / PART 1 FOLIO 9 | - | NO | - | NI (NOT INSULATED) | - | - | 0 | °C | - | 400 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM531/P20 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | HC | OTHER | 0.79 | 3.5 | 135 | 390 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5042-SP
- | - | - | - | 4 | - | 1 | - | 660TW5041 | - | FROM 660 C 5001 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5041 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | PP | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-24"-P-2002.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TC5042 | - | 660C5001 - 660TT5042 | CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660T5042 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TE5042 | - | 660 C 5001 | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5042 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5043 | - | PRODUCT FRACTIONATOR TRAY #65 | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 300 | - | C | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5043 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-441 / PART 1 FOLIO 9 | - | NO | - | NI (NOT INSULATED) | - | - | 0 | °C | - | 300 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM531/P21 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | HC | OTHER | 0.79 | 3.5 | 135 | 390 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5043-SP
- | - | - | - | 4 | - | 1 | - | 660TW5042 | - | 660 C 5001 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5042 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-441 / PART 1 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5043 | - | 660 C 5001 | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5043 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5043 | - | 660C5001 - 660TT5043 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5043 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TT5151 | - | TEMPERATURE FROM 660G5001A/B | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 400 | - | c | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5151 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 2 | - | NO | - | CC | - | - | 0 | °C | - | 400 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM531/P22 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-10"-P-2009.1-3BB3 | HC | L | 9 | 19 | 357 | 390 | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5151-SP
- | - | - | - | 4 | - | 1 | - | 660TW5043 | - | 660 C 5001 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5043 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-441 / PART 1 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5044 | - | 660 C 5001 | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5044 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5044 | - | 660C5001 - 660TT5044 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5044 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5045 | - | PRODUCT FRACTIONATOR | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5045 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 2 | - | NO | - | CC | - | - | 0 | °C | - | 350 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM538/P08 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-8"-P-2003.0-1BB1 | OTHER | L | 0.82 | 6 | 213 | 310 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5045-SP
- | - | - | - | 4 | - | 1 | - | 660TW5044 | - | 660 C 5001 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5044 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-441 / PART 1 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5045 | - | FROM 660 C 5001 | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5045 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-8"-P-2003.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5045 | - | FROM 660C5001 - 660TT5045 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5045 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5046 | - | PRODUCT FRACTIONATOR FEED | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 350 | - | C | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5046 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 2 | - | NO | - | CC | - | - | 0 | °C | - | 350 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM538/P09 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-12"-P-2000.0-1CB3 | OTHER | L | 1.1 | 7 | 287 | 320 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5046-SP
- | - | - | - | 4 | - | 1 | - | 660TW5045 | - | FROM 660 C 5001 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0202 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5045 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-8"-P-2003.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5046 | - | TO 660 C 5001 | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5046 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-12"-P-2000.0-1CB3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5046 | - | TO 660C5001 - 660TT5046 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5046 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5047 | - | PRODUCT FRACTIONATOR TRAY #39 | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 400 | - | c | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5047 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-441 / PART 1 FOLIO 9 | - | NO | - | NI (NOT INSULATED) | - | - | 0 | °C | - | 400 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM538/P10 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | HC | OTHER | 1.4 | 4.5 | 352 | 390 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5047-SP
- | - | - | - | 4 | - | 1 | - | 660TW5046 | - | TO 660 C 5001 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5046 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-12"-P-2000.0-1CB3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5047 | - | 660 C 5001 | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5047 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5047 | - | 660C5001 - 660TT5047 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5047 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5048 | - | PRODUCT FRACTIONATOR TRAY #1 | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 400 | - | C | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5048 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-441 / PART 1 FOLIO 9 | - | NO | - | NI (NOT INSULATED) | - | - | 0 | °C | - | 400 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM538/P11 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | HC | OTHER | 1.4 | 4.5 | 352 | 390 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5048-SP
- | - | - | - | 4 | - | 1 | - | 660TW5047 | - | 660 C 5001 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5047 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-441 / PART 1 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5048 | - | 660 C 5001 | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5048 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5048 | - | 660C5001 - 660TT5048 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5048 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5049 | - | SUCTION OF PRODUCT FRACTIONATOR REBOILER PUMPS | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 400 | - | C | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5049 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 2 | - | NO | - | CC | - | - | 0 | °C | - | 400 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM538/P12 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-18"-P-2006.0-3BB3 | OTHER | L | 1.89 | 5.2 | 356 | 390 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5049-SP
- | - | - | - | 4 | - | 1 | - | 660TW5048 | - | 660 C 5001 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5048 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-441 / PART 1 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5049 | - | FROM 660 C 5001 | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5049 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-18"-P-2006.0-3BB3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5049 | - | TO 660C5001 - 660TT5049 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5049 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5103 | 660-TT 5123 | PRODUCT FRACTIONATOR CONDENSER | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 100 | - | C | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5103 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 2 | - | NO | - | NI (NOT INSULATED) | - | - | 0 | °C | - | 100 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM538/P13 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-16"-P-2030.0-1BB1 | OTHER | L | 0.36 | 4 | 40 | 120 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5103-SP
- | - | - | - | 4 | - | 1 | - | 660TW5049 | - | FROM 660 C 5001 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5049 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-18"-P-2006.0-3BB3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5050 | - | 660-F-5001 PRODUCT FRAC. REBOILER PASS. | THERMO SKIN | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5050 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | N | - | - | - | - | - | - | - | -260 | °C | - | 1260 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5050 | - | 660F5001 PRODUCT FRAC. REBOILER PASS - 660TT5050 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5050 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5301 | - | COMBUSTION AIR FROM AIR PREHEATING SYSTEM | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 350 | - | c | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5301 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-441 / PART 1 FOLIO 9 | - | NO | - | NI (NOT INSULATED) | - | - | 0 | °C | - | 350 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM532/P16 | - | E10201 | - | - | - | - | - | - | - | - | - | DUCTS | OTHER | OTHER | 0.01 | 2.5 | 310 | 330 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5301-SP
- | - | - | - | 4 | - | 1 | - | 660TAH5050 | - | FROM 660F5001 - 660TT5050 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | Alarm H (535) | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5050 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5051 | - | 660-F-5001 PRODUCT FRAC. REBOILER PASS. | THERMO SKIN | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | Alarm H: 535 | - | - | - | 2 | 660T5051 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5051 | - | 660F5001 PRODUCT FRAC. REBOILER PASS - 660TT5051 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5051 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5302 | - | COMBUSTION AIR PREHEATER - AIR OUTLET | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 350 | - | c | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5302 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-441 / PART 1 FOLIO 9 | - | NO | - | NI (NOT INSULATED) | - | - | 0 | °C | - | 350 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM532/P17 | - | E10201 | - | - | - | - | - | - | - | - | - | DUCTS | OTHER | OTHER | 0.01 | 2.5 | 310 | 330 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5302-SP
- | - | - | - | 4 | - | 1 | - | 660TAH5051 | - | FROM 660F5001 - 660TT5051 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | Alarm H (535) | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5051 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5052 | - | 660-F-5001 PRODUCT FRAC. REBOILER PASS. | THERMO SKIN | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5052 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | N | - | - | - | - | - | - | - | -260 | °C | - | 1260 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5052 | - | 660F5001 PRODUCT FRAC. REBOILER PASS - 660TT5052 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5052 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660PV5308 | - | TO 660 F 5001 | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660P5308 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | CI1/CI9 | NO | - | NI (NOT INSULATED) | - | - | 0 | % | - | 100 | % | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM532/P18 | - | E10201 | 660IADM511/01 | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TAH5052 | - | FROM 660F5001 - 660TT5052 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | Alarm H (535) | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5052 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5053 | - | 660-F-5001 PRODUCT FRAC. REBOILER PASS. | THERMO SKIN | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | Alarm H: 535 | - | - | - | 2 | 660T5053 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5053 | - | 660F5001 PRODUCT FRAC. REBOILER PASS - 660TT5053 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5053 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PT5315 | 660-PG -5315 | PRODUCT FRACTIONATOR REBOILER | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 40 | - | mbar | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5315 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 3 | CI2 | NO | - | NI (NOT INSULATED) | - | - | 0 | mbar | - | 40 | mbar | - | -50 | mbar | - | 50 | mbar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM532/P19 | - | E10201 | - | - | - | - | - | - | - | - | - | DUCTS | OTHER | OTHER | 0.02 | 2.5 | 15 | 61 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PT -5315-SP
- | - | - | - | 4 | - | 1 | - | 660TAH5053 | - | FROM 660F5001 - 660TT5053 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | Alarm H (535) | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5053 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5071 | - | TEMPERATURE FROM PUMP 660G5001A | THERMOCOUPLE | - | - | - | - | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5071 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | P | LP | TV3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-18"-P-2201.0-3BB3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-TE -5071-SP
- | - | - | - | 2 | - | 1 | - | 660TTS5071 | - | TEMPERATURE TO PUMP 660G5001A | TEMPERATURE CONV | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | 0 | 400 | - | c | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5071 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 2 | - | P | LP | TV3 | - | - | 0 | °C | - | 400 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS531/P08 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-18"-P-2201.0-3BB3 | HC | OTHER | 1.5 | 19 | 356 | 390 | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5071-SP
- | - | - | - | 3 | - | 1 | - | 660TW5071 | - | TEMPERATURE FROM PUMP 660G5001A | THERMOWELL | - | - | - | - | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5071 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | P | LP | TV3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-18"-P-2201.0-3BB3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-TW -5071-SP
- | - | - | - | 4 | - | 1 | - | 660TI5071 | - | TEMPERATURE FROM PUMP 660G5001A - 660TTS5071 | BI-METAL THERMOMETER | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5071 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | LP | TV3 | - | - | - | - | - | - | - | - | - | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | HC | OTHER | 1.5 | 19 | 356 | 390 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-TI -5071-SP
- | - | - | - | 5 | - | 1 | - | 660TSLL5071 | - | TEMPERATURE FROM PUMP 660G5001A - 660TTS5071 | ALARM | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660T5071 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | LP | TV3 | - | - | - | - | - | - | - | - | - | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5072 | - | TEMPERATURE FROM PUMP 660G5001B | THERMOCOUPLE | - | - | - | - | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5072 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | P | LP | TV3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-18"-P-2202.0-3BB3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-TE -5072-SP
- | - | - | - | 2 | - | 1 | - | 660TTS5072 | - | TEMPERATURE TO PUMP 660G5001B | TEMPERATURE CONV | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | 0 | 400 | - | °C | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5072 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 2 | - | P | LP | TV3 | - | - | 0 | °C | - | 400 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS531/P09 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-18"-P-2202.0-3BB3 | HC | OTHER | 1.5 | 19 | 356 | 390 | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5072-SP
- | - | - | - | 3 | - | 1 | - | 660TW5072 | - | TEMPERATURE FROM PUMP 660G5001B | THERMOWELL | - | - | - | - | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5072 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | P | LP | TV3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-18"-P-2202.0-3BB3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-TW -5072-SP
- | - | - | - | 4 | - | 1 | - | 660TI5072 | - | TEMPERATURE FROM PUMP 660G5001B - 660TTS5072 | BI-METAL THERMOMETER | - | - | - | N | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5072 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | HC | OTHER | 1.5 | 19 | 356 | 390 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-TI -5072-SP
- | - | - | - | 5 | - | 1 | - | 660TSLL5072 | - | TEMPERATURE FROM PUMP 660G5001B - 660TTS5072 | ALARM | - | - | - | N | - | CRD | SdC | SIS | S-PLC | - | - | - | Low-Low Alarm (346) | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660T5072 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5087 | - | FROM 660 F 5001 | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5087 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2010.1-3BB3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TW5087 | - | FROM 660 F 5001 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5087 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2010.1-3BB3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-TW -5087-SP
- | - | - | - | 4 | - | 1 | - | 660TI5087 | - | FROM 660F5001 - 660TT5087 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5087 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PT5310 | 660-PG -5310 | 660K5001 FLUE GAS PRESSURE | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 3 | - | mbar Gage | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5310 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 3 | CI2 | NO | - | NI (NOT INSULATED) | - | - | 0 | mbar | Gage | 3 | mbar | Gage | -50 | mbar | Gage | 50 | mbar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM532/P20 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660TAH5087 | - | FROM 660F5001 - 660TT5087 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | High Alarm (383) | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5087 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5088 | - | FROM 660 F 5001 | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5088 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DUCTS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PT5394 | 660-PG -5394 | PRODUCT FRACTIONATOR REBOILER | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 20 | - | mbar | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5394 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 3 | CI2 | NO | - | CC | - | - | 0 | mbar | - | 20 | mbar | - | -50 | mbar | - | 50 | mbar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM532/P21 | - | E10201 | - | - | - | - | - | - | - | - | - | DUCTS | OTHER | OTHER | 0.01 | 2.5 | 310 | 330 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PT -5394-SP
- | - | - | - | 3 | - | 1 | - | 660TW5088 | - | FROM 660 F 5001 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5088 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-441 / PART 1 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DUCTS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-TW -5088-SP
- | - | - | - | 4 | - | 1 | - | 660TI5088 | - | FROM 660F5001 - 660TT5088 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5088 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5089 | - | FROM 660 F 5001 | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5089 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DUCTS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PT5399 | 660-PG -5399 | PRODUCT FRACTIONATOR REBOILER | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -10 | 10 | - | mbar | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660P5399 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 3 | CI2 | NO | - | NI (NOT INSULATED) | - | - | -10 | mbar | - | 10 | mbar | - | -50 | mbar | Gage | 50 | mbar | Gage | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM532/P22 | - | E10201 | - | - | - | - | - | - | - | - | - | DUCTS | FG | OTHER | 0 | 2.5 | 371 | 430 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PT -5399-SP
- | - | - | - | 3 | - | 1 | - | 660TW5089 | - | FROM 660 F 5001 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5089 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-441 / PART 1 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DUCTS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-TW -5089-SP
- | - | - | - | 4 | - | 1 | - | 660TI5089 | - | FROM 660F5001 - 660TT5089 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5089 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TSV5101 | - | 660-K-5001 Lube Oil system-Cooler Tube side | THER RELIEF VALVE | - | - | - | N | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660T5101 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-3"-ER-2243.0-1BW1 | WATER COOLING | L | - | 6.5 | - | 60 | - | - | - | - | IV | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-TSV -5101-SP
- | - | - | - | 1 | - | 1 | - | 660TE5103 | 660-TE 5123 | TO 660-E-5006 | RTD | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5103 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-16"-P-2030.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5103 | 660-TI 5123 | TO 660E5006 - 660TT5103 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5103 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5225 | - | FRACTIONATOR FEED EXCHANGER | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 350 | - | c | 214359C-6602-PID-0021-0201 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5225 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 2 | - | NO | - | CC | - | - | 0 | °C | - | 350 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM530/P18 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-10"-P-2000.0-1CB3 | OTHER | L | 1.9 | 7 | 298 | 320 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5225-SP
- | - | - | - | 4 | - | 1 | - | 660TW5103 | 660-TW 5123 | TO 660-E-5006 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5103 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-16"-P-2030.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660TAH5103 | - | TO 660E5006 - 660TT5103 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | High alarm (45) | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5103 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TG5116 | - | API PLAN PUMP 660G5001B | THERMOMETER | - | - | - | N | - | L | - | - | - | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5116 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TG5117 | - | API PLAN PUMP 660G5001A | THERMOMETER | - | - | - | N | - | L | - | - | - | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5117 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5226 | - | FRACTIONATOR FEED EXCHANGER | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 350 | - | c | 214359C-6602-PID-0021-0201 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5226 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 2 | - | NO | - | CC | - | - | 0 | °C | - | 350 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM530/P19 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-6"-P-2001.0-3BB3 | OTHER | L | 5.74 | 19 | 260 | 343 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5226-SP
- | - | - | - | 1 | - | 1 | - | 660TE5121 | - | TO 660-E-5003 | RTD | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0209 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5121 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD RC INS 440_PART 2_FOLIO 3 | CI1 | HOLD | HOLD | CC | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-4"-P-2021.0-3BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5121 | - | TO 660-E-5003 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0209 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5121 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5121 | - | TO 660-E-5003 | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0209 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5121 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD RC INS 440_PART 3_FOLIO 4 | CI6 | HOLD | HOLD | CC | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-4"-P-2021.0-3BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TW5121 | - | TO 660-E-5003 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0209 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5121 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD RC INS 440_PART 1_FOLIO 11 | CI1 | HOLD | HOLD | CC | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-4"-P-2021.0-3BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TAH5122 | - | BIOJET TO TANK FARM - 660TT5122 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | Alarm high (204) | - | 214359C-6602-PID-0021-0209 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5122 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TE5122 | - | BIOJET TO TANK FARM | RTD | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0209 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5122 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-4"-P-2021.0-3BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TI5122 | - | BIOJET TO TANK FARM - 660TT5122 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0209 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5122 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PT5287 | - | API PLAN PUMP 660G5002A | PRESSURE TRANSMITTER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -1 | 35 | - | Barg | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5287 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM530/P21 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660TW5122 | - | BIOJET TO TANK FARM | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | High alarm (204) | - | 214359C-6602-PID-0021-0209 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5122 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-4"-P-2021.0-3BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 19 | - | 1 | - | 660TAH5123 | - | TO 660E5007 - 660TTS5123ABC | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | High Alarm (45) | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5123 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 16 | - | 1 | - | 660TAHH5123 | - | TO 660E5007 - 660TTS5123ABC | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | High Alamr (60) | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5123 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 17 | - | 1 | - | 660TAX5123 | - | TO 660E5007 - 660TTS5123ABC | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5123 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TE5123A | - | TO 660-E-5007 | THERMOCOUPLE | - | - | - | - | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5123 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | P | LP | TV3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-14"-P-2028.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660TE5123B | L | TO 660-K-5001 | THERMOCOUPLE | - | - | - | - | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5123 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | P | LP | TV3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-14"-P-2028.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660TE5123C | - | TO 660-E-5007 | THERMOCOUPLE | - | - | - | - | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5123 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | P | LP | TV3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-14"-P-2028.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 10 | - | 1 | - | 660TI5123A | - | TO 660E5007 - 660TTS5123ABC | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | Alarm H: 45 Alarm HH: 48 | - | - | - | 5 | 660T5123 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 11 | - | 1 | - | 660TI5123B | - | TO 660E5007 - 660TTS5123ABC | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | Alarm H: 45 Alarm HH: 48 | - | - | - | 5 | 660T5123 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 12 | - | 1 | - | 660TI5123C | - | TO 660E5007 - 660TTS5123ABC | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | Alarm H: 45 Alarm HH: 48 | - | - | - | 5 | 660T5123 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 18 | - | 1 | - | 660TSH5123 | - | TO 660E5007 - 660TTS5123ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1C | SIS | DCS | - | - | - | 45 | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660T5123 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 13 | - | 1 | - | 660TSHH5123A | - | TO 660E5007 - 660TTS5123ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | High alarm (45) / High High Alarm (60) | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660T5123 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 14 | - | 1 | - | 660TSHH5123B | - | TO 660E5007 - 660TTS5123ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | High alarm (45) / High High Alarm (60) | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660T5123 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 15 | - | 1 | - | 660TSHH5123C | - | TO 660E5007 - 660TTS5123ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | High alarm (45) / High High Alarm (60) | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660T5123 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TTS5123A | - | FRACTIONATOR OFF-GAS COMPRESSOR | TEMPERATURE CONV | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | 0 | 100 | - | °C | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5123 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 2 | - | P | LP | TV3 | - | - | 0 | °C | - | 100 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS533/P07 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-14"-P-2028.0-1BB1 | OTHER | OTHER | 0.25 | 4 | 40 | 160 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TTS -5123A-SP
- | - | - | - | 3 | - | 1 | - | 660TTS5123B | - | FRACTIONATOR OFF-GAS COMPRESSOR | TEMPERATURE CONV | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | 0 | 100 | - | °C | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5123 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 2 | - | P | LP | TV3 | - | - | 0 | °C | - | 100 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS533/P08 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-14"-P-2028.0-1BB1 | OTHER | OTHER | 0.25 | 4 | 40 | 160 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TTS -5123B-SP
- | - | - | - | 1 | - | 1 | - | 660TTS5123C | 660-TT -5123 | FRACTIONATOR OFF-GAS COMPRESSOR | TEMPERATURE CONV | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | 0 | 100 | - | °C | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5123 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 2 | - | P | LP | TV3 | - | - | 0 | °C | - | 100 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS539/P04 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-14"-P-2028.0-1BB1 | OTHER | OTHER | 0.25 | 4 | 40 | 160 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5123-SP
- | - | - | - | 7 | - | 1 | - | 660TW5123A | - | TO 660-E-5007 | THERMOWELL | - | - | - | - | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5123 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | P | LP | TV3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-14"-P-2028.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-TW -5123A-SP
- | - | - | - | 8 | - | 1 | - | 660TW5123B | - | TO 660-E-5007 | THERMOWELL | - | - | - | - | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5123 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | P | LP | TV3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-14"-P-2028.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-TW -5123B-SP
- | - | - | - | 9 | - | 1 | - | 660TW5123C | - | TO 660-E-5007 | THERMOWELL | - | - | - | - | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5123 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | P | LP | TV3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-14"-P-2028.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-TW -5123C-SP
- | - | - | - | 1 | - | 1 | - | 660TE5124 | - | TO 660-G-5003A/B | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5124 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-10"-P-2027.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5124 | - | TO 660-G-5003A/B | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5124 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5124 | - | PRODUCT FRACTIONATOR RECEIVER | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 100 | - | c | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5124 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 2 | - | NO | - | NI (NOT INSULATED) | - | - | 0 | °C | - | 100 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM533/P07 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-10"-P-2027.0-1BB1 | OTHER | L | 0.73 | 4.5 | 40 | 120 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5124-SP
- | - | - | - | 4 | - | 1 | - | 660TW5124 | - | TO 660-G-5003A/B | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5124 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-10"-P-2027.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TTS5125A | - | FRACTIONATOR OFF-GAS COMPRESSOR | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1D | SIS | S-PLC | - | 0 | 100 | - | °C | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5125 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 2 | - | NO | - | PP | - | - | 0 | °C | - | 200 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS533/P09 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-6"-P-2035.0-1BB1 | OTHER | OTHER | 6.62 | 8.5 | 179 | 200 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TTS -5125A-SP
- | - | - | - | 2 | - | 1 | - | 660TTS5125B | - | FRACTIONATOR OFF-GAS COMPRESSOR | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1D | SIS | S-PLC | - | 0 | 100 | - | °C | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5125 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 2 | - | NO | - | PP | - | - | 0 | °C | - | 200 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS533/P10 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-6"-P-2035.0-1BB1 | OTHER | OTHER | 6.62 | 8.5 | 179 | 200 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TTS -5125B-SP
- | - | - | - | 3 | - | 1 | - | 660TTS5125C | - | FRACTIONATOR OFF-GAS COMPRESSOR | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1D | SIS | S-PLC | - | 0 | 100 | - | °C | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5125 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 2 | - | NO | - | PP | - | - | 0 | °C | - | 200 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS539/P05 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-6"-P-2035.0-1BB1 | OTHER | OTHER | 6.62 | 8.5 | 179 | 200 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TTS -5125C-SP
- | - | - | - | 4 | - | 1 | - | 660TE5125A | - | TO 660-E-5007 | THERMOCOUPLE | - | - | - | N | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5125 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | PP | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2035.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660TE5125B | - | TO 660-E-5007 | THERMOCOUPLE | - | - | - | N | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5125 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | PP | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2035.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660TE5125C | - | TO 660-E-5007 | THERMOCOUPLE | - | - | - | N | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5125 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | PP | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2035.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 1 | - | 660TW5125A | - | TO 660-E-5007 | THERMOWELL | - | - | - | N | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5125 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | PP | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2035.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 1 | - | 660TW5125B | - | TO 660-E-5007 | THERMOWELL | - | - | - | N | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5125 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | PP | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2035.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 9 | - | 1 | - | 660TW5125C | - | TO 660-E-5007 | THERMOWELL | - | - | - | N | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5125 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | PP | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2035.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 10 | - | 1 | - | 660TI5125A | - | TO 660E5007 - 660TTS5125ABC | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | Alarm HH: 190 Alarm H: 185 | - | - | - | 5 | 660T5125 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 11 | - | 1 | - | 660TI5125B | - | TO 660E5007 - 660TTS5125ABC | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | Alarm HH: 190 Alarm H: 185 | - | - | - | 5 | 660T5125 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 12 | - | 1 | - | 660TI5125C | - | TO 660E5007 - 660TTS5125ABC | INDICATION | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | Alarm HH: 190 Alarm H: 185 | - | - | - | 5 | 660T5125 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 13 | - | 1 | - | 660TSHH5125A | - | TO 660E5007 - 660TTS5125ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | High alarm (190) / High High Alarm (160) | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660T5125 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 14 | - | 1 | - | 660TSHH5125B | - | TO 660E5007 - 660TTS5125ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | High alarm (190) / High High Alarm (160) | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660T5125 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 15 | - | 1 | - | 660TSHH5125C | 660-TAH -5125C | TO 660E5007 - 660TTS5125ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1D | SIS | S-PLC | - | - | - | High alarm (190) / High High Alarm (160) | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660T5125 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 16 | - | 1 | - | 660TAHH5125 | - | TO 660E5007 - 660TTS5125ABC | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | 60 | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5125 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 17 | - | 1 | - | 660TAX5125 | 660-TAH -5125B | TO 660E5007 - 660TTS5125ABC | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5125 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 18 | - | 1 | - | 660TSH5125 | - | TO 660E5007 - 660TTS5125ABC | SOFT THRESHOLD | - | - | - | N | - | ITR | ST1C | SIS | DCS | - | - | - | 190 | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660T5125 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 19 | - | 1 | - | 660TAH5125 | - | TO 660E5007 - 660TTS5125ABC | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | 45 | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5125 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TAH5126 | - | FROM 660E5007 - 660TT5126 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | High Alarm 45 | - | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5126 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TE5126 | - | FROM 660-E-5007 | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5126 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2040.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TI5126 | - | FROM 660E5007 - 660TT5126 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5126 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660FT5269B | - | FUEL GAS FROM OSBL | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 1749 | - | kg/h | 214359C-6602-PID-0041-0002 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5269 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-420 / PART 3 FOLIO 4 | CΙ2 | NO | - | NI (NOT INSULATED) | - | - | 0 | mbar | - | 250 | mbar | - | -1000 | mbar | - | 1000 | mbar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM536/P15 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-3"-FG-2081.0-1BB1 | GN | OTHER | 3 | 3.5 | 41 | 75 | - | - | - | - | PED Fluid Group: 1. Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FT -5269B-SP
- | - | - | - | 5 | - | 1 | - | 660TW5126 | - | FROM 660-E-5007 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5126 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2040.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5127 | - | FROM 660-E-5008 | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0216 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5127 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-8"-P-2048.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5127 | - | FROM 660E5008 - 660TT5127 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0216 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5127 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PT5248 | - | API PLAN PUMP 660G0002 | PRESSURE TRANSMITTER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 30 | - | bar | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5248 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM534/P23 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TW5127 | - | FROM 660-E-5008 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0216 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5127 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-8"-P-2048.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5151 | - | TEMPERATURE FROM 660G5001A/B | THERMOCOUPLE | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5151 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-10"-P-2009.1-3BB3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660FT5156 | - | TO 660-C-5001 | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 172 | - | m³/h | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5156 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-420 / PART 2 FOLIO 18 | CΙ6 | - | - | NI (NOT INSULATED) | - | - | 0 | mbar | - | 250 | mbar | - | -1000 | mbar | - | 1000 | mbar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM531/P23 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-6"-P-2032.1-1BB1 | OTHER | L | 7.6 | 13.5 | 40 | 120 | - | - | - | - | PED Fluid Group: 1. Phase: Liquid. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FT -5156-SP
- | - | - | - | 3 | - | 1 | - | 660TW5151 | - | TEMPERATURE FROM 660G5001A/B | THERMOWELL | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5151 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-10"-P-2009.1-3BB3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-TW -5151-SP
- | - | - | - | 4 | - | 1 | - | 660TI5151 | - | TEMPERATURE FROM 660G5001AB - 660TT5151 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5151 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | 660TSV5160 | 660-TSV -2160 | API PLAN PUMP 660G5001A | THER RELIEF VALVE | - | - | - | N | - | L | - | - | - | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660T5160 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | TV3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | IV | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TG5162 | - | API PLAN PUMP 660G5001B | THERMOMETER | - | - | - | N | - | L | - | - | - | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5162 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TG5166 | - | API PLAN PUMP 660G5001A | THERMOMETER | - | - | - | N | - | L | - | - | - | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5166 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | 660TT5111 | - | API PLAN 5001A | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 150 | High Alaam (75°C) | °C | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5001 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM538/P16 | - | E10201 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TG5216 | - | API PLAN PUMP 660G5001A | THERMOMETER | - | - | - | N | - | L | - | - | - | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5216 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TG5217 | - | API PLAN PUMP 660G5001A | THERMOMETER | - | - | - | N | - | L | - | - | - | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5217 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 0 | - | 1 | - | 660TT5118 | - | API PLAN 5001A | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -60 | 180 | High Alaam (120°C) | °C | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5118 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM538/P17 | - | E10201 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5221 | - | TO 660 D 0004 | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5221 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2060.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5221 | - | TO 660D0004 - 660TT5221 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5221 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5229 | - | DEBUTANIZER | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 100 | - | c | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5229 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 2 | - | NO | - | NI (NOT INSULATED) | - | - | 0 | °C | - | 100 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM535/P12 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-3"-P-2219.0-1BB1 | OTHER | L | 5.4 | 6 | 40 | 180 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5229-SP
- | - | - | - | 4 | - | 1 | - | 660TW5221 | - | TO 660 D 0004 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0217 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5221 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2060.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5225 | - | FROM 660 E 5001 | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0201 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5225 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-10"-P-2000.0-1CB3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5225 | - | FROM 660E5001 - 660TT5225 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0201 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5225 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PT5289 | - | API PLAN PUMP 660G5002B | PRESSURE TRANSMITTER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -1 | 35 | - | Barg | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5289 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM530/P22 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TW5225 | - | FROM 660 E 5001 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0201 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5225 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-10"-P-2000.0-1CB3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5226 | - | FROM 660 E 5001 | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0201 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5226 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2001.0-3BB3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5226 | - | FROM 660E5001 - 660TT5226 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0201 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5226 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5230 | - | LP STEAM FROM OSBL | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 200 | - | c | 214359C-6602-PID-0041-0002 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5230 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 2 | - | NO | - | CC | - | - | 0 | °C | - | 200 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM538/P14 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-6"-VB-2066.0-1BS1 | STEAM LP | OTHER | 4.1 | 5.5 | 170 | 200 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5230-SP
- | - | - | - | 4 | - | 1 | - | 660TW5226 | - | FROM 660 E 5001 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0201 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5226 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2001.0-3BB3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660TAH5226 | - | FROM 660E5001 - 660TT5226 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | High Alamr (265) | - | 214359C-6602-PID-0021-0201 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5226 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5229 | - | FROM 660 G 5003A/B | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5229 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-3"-P-2219.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5229 | - | FROM 660G5003AB - 660TT5229 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5229 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5231 | - | MP STEAM FROM OSBL | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0041-0002 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5231 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD RC INS 440_PART 3_FOLIO 4 | CI6 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TW5229 | - | FROM 660 G 5003A/B | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0215 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5229 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-3"-P-2219.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5230 | - | LP STEAM FROM OSBL | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0041-0002 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5230 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-VB-2066.0-1BS1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5230 | - | LP STEAM FROM OSBL - 660TT5230 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0041-0002 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5230 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5232 | - | UTILITIES BATTERY LIMIT | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 100 | - | c | 214359C-6602-PID-0041-0002 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5232 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 2 | - | NO | - | NI (NOT INSULATED) | - | - | 0 | °C | - | 100 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM538/P15 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-16"-SB-2073.0-1CH3 | OTHER | OTHER | 0.2 | 3.5 | 40 | 337 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5232-SP
- | - | - | - | 4 | - | 1 | - | 660TW5230 | - | LP STEAM FROM OSBL | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0041-0002 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5230 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-VB-2066.0-1BS1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5231 | - | MP STEAM FROM OSBL | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0041-0002 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5231 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD RC INS 440_PART 2_FOLIO 3 | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-3"-VM-2069.0-3BS1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5231 | - | MP STEAM FROM OSBL | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0041-0002 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5231 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5236 | - | NATURAL GAS FROM BATTERY LIMIT | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 100 | - | c | 214359C-6602-PID-0041-0002 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5236 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 3 FOLIO 2 | - | NO | - | NI (NOT INSULATED) | - | - | 0 | °C | - | 100 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM536/P14 | - | E10201 | - | - | - | - | - | - | - | - | - | 600-4"-FG-1008.0-1BB1 | GN | OTHER | 2.9 | 3.5 | 41 | 75 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5236-SP
- | - | - | - | 4 | - | 1 | - | 660TW5231 | - | MP STEAM FROM OSBL | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0041-0002 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5231 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD RC INS 440_PART 1_FOLIO 11 | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-3"-VM-2069.0-3BS1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5232 | - | TO HC FLARE HEADER OSBL | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0041-0002 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5232 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-16"-SB-2073.0-1CH3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5232 | - | TO HC FLARE HEADER OSBL - 660TT5232 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0041-0002 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5232 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TT5281 | - | API PLAN 5002A | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -20 | 300 | - | °C | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5281 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM530/P23 | - | E10201 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TW5232 | - | TO HC FLARE HEADER OSBL | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0041-0002 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5232 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-16"-SB-2073.0-1CH3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5236 | - | FUEL GAS FROM OSBL | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0041-0002 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5236 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 600-4"-FG-1008.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5236 | - | FUEL GAS FROM OSBL - 660TT5232 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0041-0002 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5236 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HV5220 | - | 660 E 5002 | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660H5220 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM536/P16 | - | E10201 | 660IADM513/08 | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TW5236 | - | FUEL GAS FROM OSBL | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0041-0002 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5236 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 600-4"-FG-1008.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TSV5261 | - | API PLAN PUMP 660G5001B | THER RELIEF VALVE | - | - | - | N | - | L | - | - | - | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660T5261 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | TV3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | IV | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TG5262 | - | API PLAN PUMP 660G5001A | THERMOMETER | - | - | - | N | - | L | - | - | - | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5262 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TSV5263 | - | 660-E-5007 Tube Side | THER RELIEF VALVE | - | - | - | N | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660T5263 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | P | LP | TV3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-4"-ER-2039.1-1BB1 | WATER COOLING | L | - | 7 | - | 60 | - | - | - | - | IV | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-TSV -5263-SP
- | - | - | - | 1 | - | 1 | - | 660TG5266 | - | API PLAN PUMP 660G5001A | THERMOMETER | - | - | - | N | - | L | - | - | - | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5266 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660FT5057 | - | PROCESS FLUID TO 660E5008 | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 60 | - | m³/h | 214359C-6602-PID-0021-0208 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660F5057 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD RC INS 420 / PART 2 FOLIO 18 | CΙ6 | - | - | CC | - | - | 0 | mbar | - | 250 | mbar | - | -1000 | mbar | - | 1000 | mbar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM530/P24 | - | E10201 | - | - | - | - | - | - | - | - | - | 660-4"-P-2016.1-3BB3 | KERO | L | 7.71 | 19 | 217 | 280 | - | - | - | - | PED Fluid Group: 1. Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-FT -5057-SP
- | - | - | - | 1 | - | 1 | - | 660TT5282 | - | API PLAN 5002A | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -20 | 300 | - | °C | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5282 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM538/P20 | - | E10201 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TG5283 | - | API PLAN PUMP 660G5002A | THERMOMETER | - | - | - | N | - | L | - | - | - | - | - | - | - | - | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5283 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TSV5284 | - | API PLAN PUMP 660G5002A | THER RELIEF VALVE | - | - | - | N | - | L | - | - | - | - | - | - | - | - | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660T5284 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | TV3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | IV | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TG5285 | - | API PLAN PUMP 660G5002B | THERMOMETER | - | - | - | N | - | L | - | - | - | - | - | - | - | - | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5285 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TSV5286 | - | API PLAN PUMP 660G5002B | THER RELIEF VALVE | - | - | - | N | - | L | - | - | - | - | - | - | - | - | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660T5286 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | TV3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | IV | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TT5295 | - | API PLAN 5002B | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -20 | 300 | - | °C | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5295 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM538/P21 | - | E10201 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TT5296 | - | API PLAN 5002B | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -20 | 300 | - | °C | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5296 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM538/P22 | - | E10201 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5301 | - | AIR TO 660 F 5001 | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5301 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DUCTS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5301 | - | AIR TO 660F5001 - 660TT5301 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5301 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660FL5387 | - | HOLD | FLOW SWTICH | - | - | - | N | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660F5387 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | EXT_230V | NR | - | - | - | - | - | - | - | - | - | 660BJM532/P23 | - | E10202* | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TW5301 | - | AIR TO 660 F 5001 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5301 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DUCTS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5302 | - | AIR TO 660 F 5001 | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5302 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DUCTS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5302 | - | AIR TO 660F5001 - 660TT5302 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5302 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660FL5388 | - | HOLD | FLOW SWTICH | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660F5388 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | EXT_230V | NR | - | - | - | - | - | - | - | - | - | 660BJM532/P24 | - | E10202* | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TW5302 | - | AIR TO 660 F 5001 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5302 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DUCTS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5303 | - | FROM 660 E 5010 TO 660 E 5012 | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5303 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DUCTS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5303 | - | FROM 660E5010 TO 660E5012 - 660TT5303 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5303 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5305 | - | COMBUSTION AIR PREHEATER - AIR INLET | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 450 | - | c | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5305 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-441 / PART 1 FOLIO 9 | - | NO | - | NI (NOT INSULATED) | - | - | 0 | °C | - | 450 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM537/P09 | - | E10201 | - | - | - | - | - | - | - | - | - | DUCTS | FG | OTHER | 0 | 2.5 | 371 | 430 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5305-SP
- | - | - | - | 4 | - | 1 | - | 660TW5303 | - | FROM 660 E 5010 TO 660 E 5012 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5303 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DUCTS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660TAH5303 | - | FROM 660 E 5010 TO 660 E 5012 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | High Alarm (45) | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5303 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660TAL5303 | - | FROM 660 E 5010 TO 660 E 5012 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5303 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5304 | - | FROM 660 F 5001 | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5304 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5304 | - | FROM 660F5001 - 660TT5304 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5304 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5309 | - | COMBUSTION AIR PREHEATER | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 200 | Low Alaam (60 °C) | °C | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | Alarm L: 60 | - | - | - | 3 | 660T5309 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | HOLD | NO | - | NI (NOT INSULATED) | N | - | 0 | °C | - | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM537/P10 | - | E10201 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TW5304 | - | FROM 660 F 5001 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5304 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TBC | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660TAH5304 | - | FROM 660F5001 - 660TT5304 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | Alarm high (430) | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5304 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5305 | - | 660 F 5001 TO 600 E 5012 | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5305 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DUCTS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5305 | - | 660F5001 TO 600E5012 - 660TT5305 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5305 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5310 | - | 660 E 5012 | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 200 | Low Alaam (60 °C) | °C | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | Alarm L: 60 | - | - | - | 3 | 660T5310 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | HOLD | NO | - | NI (NOT INSULATED) | N | - | 0 | °C | - | 200 | °C | - | -260 | °C | - | 1260 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM537/P11 | - | E10201 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TW5305 | - | 660 F 5001 TO 600 E 5012 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5305 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DUCTS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660TAH5305 | - | 660F5001 TO 600E5012 - 660TT5305 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | High Alarm (376) | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5305 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5306 | - | 660 E 5012 | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5306 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD RC INS 440_PART 2_FOLIO 3 | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5306 | - | 660 E 5012 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5306 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5306 | - | 660 E 5012 | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5306 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD RC INS 441_PART 1_FOLIO 9 | HOLD | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TW5306 | - | 660 E 5012 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5306 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD RC INS 441_PART 1_FOLIO 4 | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TI5307 | - | TEMP TO 660E5012 - 660TTS5307 | INDICATION | - | - | - | N | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5307 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TTS5307 | - | COMBUSTION AIR PREHEATER - FLUE GAS OUTLET | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1D | SIS | S-PLC | - | 0 | 300 | - | °C | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5307 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-441 / PART 1 FOLIO 9 | - | NO | - | NI (NOT INSULATED) | - | - | 0 | °C | - | 300 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS538/P05 | - | E10201 | - | - | - | - | - | - | - | - | - | DUCTS | FG | OTHER | -0.01 | 2.5 | 120 | 371 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5307-SP
- | - | - | - | 3 | - | 1 | - | 660TW5307 | - | TEMP TO 660 E 5012 | THERMOWELL | - | - | - | N | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5307 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DUCTS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TE5307 | - | TEMP TO 660 E 5012 | THERMOCOUPLE | - | - | - | N | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5307 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DUCTS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660TAHH5307 | - | TEMP TO 660 E 5012 | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | High High Alarm (170) | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5307 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660TSHH5307 | - | TEMP TO 660E5012 - 660TTS5307 | ALARM | - | - | - | N | - | CRD | SdC | SIS | S-PLC | - | - | - | High High Alarm (170) | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660T5307 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5308A | 660-TE -5308 | 660 E 5012 | THERMO DUPLEX | - | - | - | N | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5308 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD RC INS 440_PART 2_FOLIO 3 | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TW5308 | - | 660 E 5012 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5308 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD RC INS 441_PART 1_FOLIO 4 | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5308 | - | 660 E 5012 | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5308 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD RC INS 441_PART 1_FOLIO 9 | HOLD | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TI5308 | - | 660 E 5012 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5308 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660TE5308B | - | 660 E 5012 | THERMO DUPLEX | - | - | - | N | - | L | ST1C | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5308 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD RC INS 440_PART 2_FOLIO 3 | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5309 | - | 660 E 5012 | THERMOCOUPLE | - | - | - | N | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5309 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | CI1 | NO | - | NI (NOT INSULATED) | N | - | - | - | - | - | - | - | -260 | °C | - | 1260 | °C | - | - | - | - | - | - | - | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TW5309 | - | 660 E 5012 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5309 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5311 | - | PRODUCT FRACTIONATOR REBOILER STACK | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 300 | - | c | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5311 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-441 / PART 1 FOLIO 9 | - | NO | - | NI (NOT INSULATED) | - | - | 0 | °C | - | 300 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM537/P12 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | OTHER | OTHER | 0 | 2.5 | 120 | 450 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5311-SP
- | - | - | - | 4 | - | 1 | - | 660TI5309 | - | 660E5012 - 660TT5309 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5309 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660TE5309B | - | 660 E 5012 | THERMO DUPLEX | - | - | - | N | - | L | ST1C | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5309 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660TAL5309 | - | 660E5012 - 660TT5309 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | Low Alaam (66°C) | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5309 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5310 | - | 660 E 5012 | THERMOCOUPLE | - | - | - | N | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | Alarm L: 60 | - | - | - | 2 | 660T5310 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | CI1 | NO | - | NI (NOT INSULATED) | N | - | 0 | °C | - | 200 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TW5310 | - | 660 E 5012 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5310 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TT5317 | - | PRODUCT FRACTIONATOR REBOILER | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 750 | - | °C | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | Alarm H: 535 | - | - | - | 3 | 660T5317 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | HOLD | NO | - | NI (NOT INSULATED) | N | - | 0 | °C | - | 750 | °C | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM537/P13 | - | E10201 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TI5310 | - | 660E5012 - 660TT5310 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5310 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660TE5310B | - | 660 E 5012 | THERMO DUPLEX | - | - | - | N | - | L | ST1C | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5310 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660TAL5310 | - | 660E5012 - 660TT5310 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | Low Alaam (66 °C) | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5310 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5311 | - | FROM 660 F 5001 | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5311 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5311 | - | FROM 660F5001 - 660TT5331 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5311 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TT5318 | - | 660-F-5001 PRODUCT FRAC. REBOILER PASS. | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 750 | - | °C | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | Alarm H: 535 | - | - | - | 3 | 660T5318 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | HOLD | NO | - | NI (NOT INSULATED) | N | - | 0 | °C | - | 750 | °C | - | -260 | °C | - | 1260 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM537/P14 | - | E10201 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TW5311 | - | FROM 660 F 5001 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5311 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TBC | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660TAH5311 | - | FROM 660F5001 - 660TT5331 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | Alarm H (430) | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5311 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TG5315 | - | FROM 660 E 5011 | THERMOMETER | - | - | - | N | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0221 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5315 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | CC | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-3"-FG-2095.0-1KB2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TW5315 | - | FROM 660 E 5051 | THERMOWELL | - | - | - | N | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0221 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5315 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | CC | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-3"-FG-2095.0-1KB2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5317 | - | 660-F-5001 | THERMO SKIN | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5317 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | N | - | - | - | - | - | - | - | -260 | °C | - | 1260 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TW5317 | - | 660-F-5001 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5317 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TI5317 | - | 660F5001 - 660TT5317 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5317 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660TAH5317 | - | 660F5001 - 660TT5317 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | Alarm H (535) | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5317 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5318 | - | 660-F-5001 | THERMO SKIN | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | Alarm H: 535 | - | - | - | 2 | 660T5318 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TW5318 | - | 660-F-5001 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5318 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | NO | - | NI (NOT INSULATED) | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TI5318 | - | 660F5001 - 660TT5318 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5318 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660TAH5318 | - | 660F5001 - 660TT5318 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | Alarm H (535) | - | 214359C-6602-PID-0021-0205 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5318 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TAH5330 | - | 660F5001 - 660TT5330 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | Alarm high (900) | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5330 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TE5330 | - | 660-F-5001 | THERMOCOUPLE | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5330 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5333 | - | 660F5001 COMPENSATION FOR 660AT5010 | TEMPERATURE CONV | - | - | - | - | - | L | Field | - | - | - | 0 | 900 | - | c | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5333 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-441 / PART 1 FOLIO 9 | - | NO | - | NI (NOT INSULATED) | - | - | 0 | °C | - | 900 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM537/P18 | - | - | - | - | - | - | - | - | - | - | - | E. | OTHER | OTHER | 0 | 2.5 | 846 | 900 | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5333-SP
- | - | - | - | 5 | - | 1 | - | 660TW5330 | - | 660-F-5001 | THERMOWELL | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5330 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TBC | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-TW -5330-SP
- | - | - | - | 11 | - | 1 | - | 660TW5331 | - | 660F5001 COMBUSTION AIR PREHEATER | THERMOWELL | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5331 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DUCTS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-TW -5331-SP
- | - | - | - | 12 | - | 1 | - | 660TE5331 | - | 660F5001 COMBUSTION AIR PREHEATER | THERMOCOUPLE | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5331 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DUCTS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 13 | - | 1 | - | 660TI5331 | - | 660F5001 COMBUSTION AIR PREHEATER - 660TT5331 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5331 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5392 | - | COMBUSTION AIR FAN | TEMPERATURE CONV | - | - | HEAD MOUNTED | N | - | L | ST1C | BPCS | DCS | - | 0 | 100 | - | c | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5392 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-441 / PART 1 FOLIO 9 | - | NO | - | NI (NOT INSULATED) | - | - | 0 | °C | - | 100 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM537/P19 | - | E10201 | - | - | - | - | - | - | - | - | - | DUCTS | OTHER | OTHER | -0.01 | 2.5 | 15 | 61 | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5392-SP
- | - | - | - | 15 | - | 1 | - | 660TAL5331 | - | 660F5001 COMBUSTION AIR PREHEATER - 660TT5331 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | Low Alaam (100°C) | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5331 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 16 | - | 1 | - | 660TAH5331 | - | 660F5001 COMBUSTION AIR PREHEATER - 660TT5331 | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | High Alaam (155°C) | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5331 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 17 | - | 1 | - | 660TC5331 | - | 660F5001 COMBUSTION AIR PREHEATER - 660TT5331 | TEMPERATURE CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660T5331 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 18 | - | 1 | - | 660TV5331 | - | 660F5001 COMBUSTION AIR PREHEATER | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660T5331 | NbO | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | % | - | 100 | % | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM537/P20 | - | E10201 | 660IADM511/02 | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 19 | - | 1 | - | 660ZT5331 | - | 660F5001 COMBUSTION AIR PREHEATER | AXIAL DISPLACEMEN | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 100 | - | % | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5331 | NbO | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | % | - | 100 | % | - | - | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM537/P21 | - | E10201 | 660IADM511/06 | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 20 | - | 1 | - | 660ZI5331 | - | 660F5001 COMBUSTION AIR PREHEATER | INDICATION | - | - | - | - | - | CR | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5331 | NbO | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5332 | - | 660F5001 COMPENSATION FOR 660AT5011 | THERMOCOUPLE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5332 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5332 | - | 660F5001 COMPENSATION FOR 660AT5011 | INDICATION | - | - | - | - | - | L | ST1C | - | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5332 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TT5332 | - | 660F5001 COMPENSATION FOR 660AT5011 | TEMPERATURE CONV | - | - | - | - | - | L | Field | - | - | - | 0 | 900 | - | c | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660T5332 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-441 / PART 1 FOLIO 9 | - | NO | - | NI (NOT INSULATED) | - | - | 0 | °C | - | 900 | °C | - | -40 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | OTHER | OTHER | 0 | 2.5 | 846 | 900 | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-TT -5332-SP
- | - | - | - | 4 | - | 1 | - | 660TW5332 | - | 660F5001 COMPENSATION FOR 660AT5011 | THERMOWELL | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5332 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TBC | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-TW -5332-SP
- | - | - | - | 1 | - | 1 | - | 660TE5333 | - | 660F5001 COMPENSATION FOR 660AT5010 | THERMOCOUPLE | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5333 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5333 | - | 660F5001 COMPENSATION FOR 660AT5010 | INDICATION | - | - | - | - | - | L | ST1C | - | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5333 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660ZT5308 | - | TO 660 F 5001 | TRANSMITTER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660Z5308 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-410 / PART 3 FOLIO 3 | HOLD | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM537/P22 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | PED Group: 1 Phase: Gas. | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TW5333 | - | 660F5001 COMPENSATION FOR 660AT5010 | THERMOWELL | - | - | - | - | - | L | - | - | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5333 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | TBC | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-TW -5333-SP
- | - | - | - | 1 | - | 1 | - | 660TAHH5381A | - | TEMPERATURE IN 660K5004 - 660TTS5381A | ALARM | - | - | - | N | - | CRD | SdC | BPCS | S-PLC | - | - | - | High Alaam (85 °C) / High High Alarm (110 °C) | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5381 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TE5381A | - | TEMPERATURE IN 660K5004 - 660TTS5381A | RTD | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5381 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | HOLD | - | - | - | - | - | - | - | - | - | -200 | °C | - | 850 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TI5381A | - | TEMPERATURE IN 660K5004 - 660TTS5381A | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5381 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TTS5381A | - | TEMPERATURE IN 660K5004 - 660TTS5381A | TEMPERATURE CONV | - | - | - | N | - | L | ST1D | BPCS | S-PLC | - | 0 | 150 | High Alarm (85) / High Alarm (110) | °C | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | Alarm HH: 110 Alarm H: 85 | - | - | - | 3 | 660T5381 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | HOLD | - | - | - | 0 | °C | - | 150 | °C | - | 0 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS538/P06 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660TAHH5381B | - | TEMPERATURE IN 660K5004 - 660TTS5381B | ALARM | - | - | - | N | - | CRD | SdC | BPCS | S-PLC | - | - | - | High Alaam (85 °C) / High High Alarm (110 °C) | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5381 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660TE5381B | - | TEMPERATURE IN 660K5004 - 660TTS5381B | RTD | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5381 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | HOLD | - | - | - | - | - | - | - | - | - | -200 | °C | - | 850 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 1 | - | 660TI5381B | - | TEMPERATURE IN 660K5004 - 660TTS5381B | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5381 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 1 | - | 660TTS5381B | - | TEMPERATURE IN 660K5004 - 660TTS5381B | TEMPERATURE CONV | - | - | - | N | - | L | ST1D | BPCS | S-PLC | - | 0 | 150 | High Alarm (85) / High Alarm (110) | °C | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | Alarm HH: 110 Alarm H: 85 | - | - | - | 3 | 660T5381 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | HOLD | - | - | - | 0 | °C | - | 150 | °C | - | 0 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS538/P07 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TAHH5382A | - | TEMPERATURE IN 660K5003 - 660TTS5382A | ALARM | - | - | - | - | - | CRD | SdC | BPCS | S-PLC | - | - | - | High Alaam (85 °C) / High High Alarm (110 °C) | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5382 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TE5382A | - | TEMPERATURE IN 660K5003 - 660TTS5382A | RTD | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5382 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | HOLD | - | - | - | - | - | - | - | - | - | -200 | °C | - | 850 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TI5382A | - | TEMPERATURE IN 660K5003 - 660TTS5382A | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5382 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TTS5382A | - | TEMPERATURE IN 660K5003 - 660TTS5382A | TEMPERATURE CONV | - | - | - | - | - | L | ST1D | BPCS | S-PLC | - | 0 | 150 | High Alarm (85) / High Alarm (110) | °C | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | Alarm HH: 110 Alarm H: 85 | - | - | - | 3 | 660T5382 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | HOLD | - | - | - | 0 | °C | - | 150 | °C | - | 0 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS532/P05 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660TAHH5382B | - | TEMPERATURE IN 660K5003 - 660TTS5382B | ALARM | - | - | - | - | - | CRD | SdC | BPCS | S-PLC | - | - | - | High Alaam (85 °C) / High High Alarm (110 °C) | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5382 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660TE5382B | - | TEMPERATURE IN 660K5003 - 660TTS5382B | RTD | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5382 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | HOLD | - | - | - | - | - | - | - | - | - | -200 | °C | - | 850 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 1 | - | 660TI5382B | - | TEMPERATURE IN 660K5003 - 660TTS5382B | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5382 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 1 | - | 660TTS5382B | - | TEMPERATURE IN 660K5003 - 660TTS5382B | TEMPERATURE CONV | - | - | - | - | - | L | ST1D | BPCS | S-PLC | - | 0 | 150 | High Alarm (85) / High Alarm (110) | °C | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | Alarm HH: 110 Alarm H: 85 | - | - | - | 3 | 660T5382 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | HOLD | - | - | - | 0 | °C | - | 150 | °C | - | 0 | °C | - | 1100 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS532/P06 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5392 | - | TEMP TO 660 K 5004 | THERMOCOUPLE | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5392 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 2 FOLIO 4 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DUCTS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TI5392 | - | TEMP TO 660K5004 - 660TT5392 | INDICATION | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5392 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660FL5389 | - | HOLD | FLOW SWTICH | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660F5389 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | EXT_230V | NR | - | - | - | - | - | - | - | - | - | 660BJM537/P23 | - | E10202* | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TW5392 | - | TEMP TO 660 K 5004 | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5392 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | STD-RC-INS-440 / PART 1 FOLIO 11 | CI1 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DUCTS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | 660-TW -5392-SP
- | - | - | - | 1 | - | 1 | - | 660TE5500A | - | 660K5001 - MACHINE PROTECTION SYSTEM | THERMO DUPLEX | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -100 | 300 | ALERT (125°C) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 125 | - | - | - | 2 | 660T5500 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | -100 | °C | - | 300 | °C | - | - | - | - | - | - | AI40 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJTS540/T01 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TE5500B | - | 660K5001 - MACHINE PROTECTION SYSTEM | THERMO DUPLEX | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -100 | 300 | ALERT (125°C) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 125 | - | - | - | 2 | 660T5500 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | -100 | °C | - | 300 | °C | - | - | - | - | - | - | AI40 | - | - | - | - | - | - | - | - | - | - | - | 660BJTS540/T02 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TI5500 | - | 660K5001 - MACHINE PROTECTION SYSTEM | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5500 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TAH5500 | - | 660K5001 - MACHINE PROTECTION SYSTEM | HIGH TEMPERATURE ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | High Alarm (125) | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5500 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5501A | - | 660K5001 - MACHINE PROTECTION SYSTEM | THERMO DUPLEX | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -100 | 300 | ALERT (125°C) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 125 | - | - | - | 2 | 660T5501 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | -100 | °C | - | 300 | °C | - | - | - | - | - | - | AI40 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJTS540/T03 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TE5501B | - | 660K5001 - MACHINE PROTECTION SYSTEM | THERMO DUPLEX | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -100 | 300 | ALERT (125°C) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 125 | - | - | - | 2 | 660T5501 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | -100 | °C | - | 300 | °C | - | - | - | - | - | - | AI40 | - | - | - | - | - | - | - | - | - | - | - | 660BJTS540/T04 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TI5501 | - | 660K5001 - MACHINE PROTECTION SYSTEM | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5501 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TAH5501 | - | 660K5001 - MACHINE PROTECTION SYSTEM | HIGH TEMPERATURE ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | High Alarm (125) | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5501 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5502A | - | 660K5001 - MACHINE PROTECTION SYSTEM | THERMO DUPLEX | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -100 | 300 | ALERT (125°C) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 125 | - | - | - | 2 | 660T5502 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | -100 | °C | - | 300 | °C | - | - | - | - | - | - | AI40 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJTS540/T05 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TE5502B | - | 660K5001 - MACHINE PROTECTION SYSTEM | THERMO DUPLEX | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -100 | 300 | ALERT (125°C) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 125 | - | - | - | 2 | 660T5502 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | -100 | °C | - | 300 | °C | - | - | - | - | - | - | AI40 | - | - | - | - | - | - | - | - | - | - | - | 660BJTS540/T06 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TI5502 | - | 660K5001 - MACHINE PROTECTION SYSTEM | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5502 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TAH5502 | - | 660K5001 - MACHINE PROTECTION SYSTEM | HIGH TEMPERATURE ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | High Alarm (125) | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5502 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5503A | - | 660K5001 - MACHINE PROTECTION SYSTEM | THERMO DUPLEX | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -100 | 300 | ALERT (125°C) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 125 | - | - | - | 2 | 660T5503 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | -100 | °C | - | 300 | °C | - | - | - | - | - | - | AI40 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJTS540/T07 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TE5503B | - | 660K5001 - MACHINE PROTECTION SYSTEM | THERMO DUPLEX | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -100 | 300 | ALERT (125°C) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 125 | - | - | - | 2 | 660T5503 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | -100 | °C | - | 300 | °C | - | - | - | - | - | - | AI40 | - | - | - | - | - | - | - | - | - | - | - | 660BJTS540/T08 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TI5503 | - | 660K5001 - MACHINE PROTECTION SYSTEM | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5503 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TAH5503 | - | 660K5001 - MACHINE PROTECTION SYSTEM | HIGH TEMPERATURE ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | High Alarm (125) | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5503 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5504A | - | 660K5001 - MACHINE PROTECTION SYSTEM | THERMO DUPLEX | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -100 | 300 | ALERT (125°C) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 125 | - | - | - | 2 | 660T5504 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | -100 | °C | - | 300 | °C | - | - | - | - | - | - | AI40 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJTS540/T09 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TE5504B | - | 660K5001 - MACHINE PROTECTION SYSTEM | THERMO DUPLEX | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -100 | 300 | ALERT (125°C) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 125 | - | - | - | 2 | 660T5504 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | -100 | °C | - | 300 | °C | - | - | - | - | - | - | AI40 | - | - | - | - | - | - | - | - | - | - | - | 660BJTS540/T10 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TI5504 | - | 660K5001 - MACHINE PROTECTION SYSTEM | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5504 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TAH5504 | - | 660K5001 - MACHINE PROTECTION SYSTEM | HIGH TEMPERATURE ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | High Alarm (125) | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5504 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5505A | - | 660K5001 - MACHINE PROTECTION SYSTEM | THERMO DUPLEX | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -100 | 300 | ALERT (125°C) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 125 | - | - | - | 2 | 660T5505 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | -100 | °C | - | 300 | °C | - | - | - | - | - | - | AI40 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJTS540/T11 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TE5505B | - | 660K5001 - MACHINE PROTECTION SYSTEM | THERMO DUPLEX | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -100 | 300 | ALERT (125°C) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 125 | - | - | - | 2 | 660T5505 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | -100 | °C | - | 300 | °C | - | - | - | - | - | - | AI40 | - | - | - | - | - | - | - | - | - | - | - | 660BJTS540/T12 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TI5505 | - | 660K5001 - MACHINE PROTECTION SYSTEM | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5505 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TAH5505 | - | 660K5001 - MACHINE PROTECTION SYSTEM | HIGH TEMPERATURE ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | High Alarm (125) | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5505 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5506A | - | 660K5001 - MACHINE PROTECTION SYSTEM | THERMO DUPLEX | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 150 | High Alarm (08) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 80 | - | - | - | 2 | 660T5506 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | 0 | °C | - | 150 | °C | - | - | - | - | - | - | AI40 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJTS530/T01 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TE5506B | - | 660K5001 - MACHINE PROTECTION SYSTEM | THERMO DUPLEX | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 150 | High Alarm (08) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 80 | - | - | - | 2 | 660T5506 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | 0 | °C | - | 150 | °C | - | - | - | - | - | - | AI40 | - | - | - | - | - | - | - | - | - | - | - | 660BJTS530/T02 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TI5506 | - | 660K5001 - MACHINE PROTECTION SYSTEM | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5506 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TAH5506 | - | 660K5001 - MACHINE PROTECTION SYSTEM | HIGH TEMPERATURE ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | High Alarm (80) | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5506 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5507A | - | 660K5001 - MACHINE PROTECTION SYSTEM | THERMO DUPLEX | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 150 | High Alarm (08) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 80 | - | - | - | 2 | 660T5507 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | 0 | °C | - | 150 | °C | - | - | - | - | - | - | AI40 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJTS530/T03 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TE5507B | - | 660K5001 - MACHINE PROTECTION SYSTEM | THERMO DUPLEX | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 150 | High Alarm (08) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 80 | - | - | - | 2 | 660T5507 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | 0 | °C | - | 150 | °C | - | - | - | - | - | - | AI40 | - | - | - | - | - | - | - | - | - | - | - | 660BJTS530/T04 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TI5507 | - | 660K5001 - MACHINE PROTECTION SYSTEM | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5507 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TAH5507 | - | 660K5001 - MACHINE PROTECTION SYSTEM | HIGH TEMPERATURE ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | High Alarm (80) | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5507 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5508A | - | 660K5001 - MACHINE PROTECTION SYSTEM | THERMO DUPLEX | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 150 | High Alarm (08) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 75 | - | - | - | 2 | 660T5508 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | 0 | °C | - | 150 | °C | - | - | - | - | - | - | AI40 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJTS530/T05 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TE5508B | - | 660K5001 - MACHINE PROTECTION SYSTEM | THERMO DUPLEX | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 150 | High Alarm (08) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 75 | - | - | - | 2 | 660T5508 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | 0 | °C | - | 150 | °C | - | - | - | - | - | - | AI40 | - | - | - | - | - | - | - | - | - | - | - | 660BJTS530/T06 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TI5508 | - | 660K5001 - MACHINE PROTECTION SYSTEM | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5508 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TAH5508 | - | 660K5001 - MACHINE PROTECTION SYSTEM | HIGH TEMPERATURE ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | High Alarm (75) | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5508 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5509A | - | 660K5001 - MACHINE PROTECTION SYSTEM | THERMO DUPLEX | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 150 | High Alarm (08) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 75 | - | - | - | 2 | 660T5509 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | 0 | °C | - | 150 | °C | - | - | - | - | - | - | AI40 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJTS530/T07 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TE5509B | - | 660K5001 - MACHINE PROTECTION SYSTEM | THERMO DUPLEX | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 150 | High Alarm (08) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 75 | - | - | - | 2 | 660T5509 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | 0 | °C | - | 150 | °C | - | - | - | - | - | - | AI40 | - | - | - | - | - | - | - | - | - | - | - | 660BJTS530/T08 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TI5509 | - | 660K5001 - MACHINE PROTECTION SYSTEM | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5509 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TAH5509 | - | 660K5001 - MACHINE PROTECTION SYSTEM | HIGH TEMPERATURE ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | High Alarm (75) | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5509 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5510A | - | 660K5001 - MACHINE PROTECTION SYSTEM | THERMO DUPLEX | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 150 | High Alarm (08) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 75 | - | - | - | 2 | 660T5510 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | 0 | °C | - | 150 | °C | - | - | - | - | - | - | AI40 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJTS530/T09 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TE5510B | - | 660K5001 - MACHINE PROTECTION SYSTEM | THERMO DUPLEX | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 150 | High Alarm (08) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 75 | - | - | - | 2 | 660T5510 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | 0 | °C | - | 150 | °C | - | - | - | - | - | - | AI40 | - | - | - | - | - | - | - | - | - | - | - | 660BJTS530/T10 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TI5510 | - | 660K5001 - MACHINE PROTECTION SYSTEM | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5510 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TAH5510 | - | 660K5001 - MACHINE PROTECTION SYSTEM | HIGH TEMPERATURE ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | High Alarm (75) | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5510 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5511A | - | 660K5001 - MACHINE PROTECTION SYSTEM | THERMO DUPLEX | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 150 | High Alarm (08) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 75 | - | - | - | 2 | 660T5511 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | 0 | °C | - | 150 | °C | - | - | - | - | - | - | AI40 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJTS530/T11 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TE5511B | - | 660K5001 - MACHINE PROTECTION SYSTEM | THERMO DUPLEX | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 150 | High Alarm (08) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 75 | - | - | - | 2 | 660T5511 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | 0 | °C | - | 150 | °C | - | - | - | - | - | - | AI40 | - | - | - | - | - | - | - | - | - | - | - | 660BJTS530/T12 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TI5511 | - | 660K5001 - MACHINE PROTECTION SYSTEM | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5511 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TAH5511 | - | 660K5001 - MACHINE PROTECTION SYSTEM | HIGH TEMPERATURE ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | High Alarm (75) | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5511 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5514 | - | 660K5001 - MACHINE PROTECTION SYSTEM | RTD | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -60 | 180 | High Alarm (120) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 120 | - | - | - | 2 | 660T5514 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | -60 | °C | - | 180 | °C | - | - | - | - | - | - | AI40 | - | - | - | - | - | - | - | - | - | - | - | 660BJTS550/TS1-P01 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5515 | - | 660K5001 - MACHINE PROTECTION SYSTEM | RTD | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -60 | 180 | High Alarm (120) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 120 | - | - | - | 2 | 660T5515 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | -60 | °C | - | 180 | °C | - | - | - | - | - | - | AI40 | - | - | - | - | - | - | - | - | - | - | - | 660BJTS550/TS1-P02 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TI5512 | - | 660K5001 - MACHINE PROTECTION SYSTEM | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5512 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TAH5512 | - | 660K5001 - MACHINE PROTECTION SYSTEM | HIGH TEMPERATURE ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | High Alarm (115) | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5512 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5516 | - | 660K5001 - MACHINE PROTECTION SYSTEM | RTD | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -60 | 180 | High Alarm (120) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 120 | - | - | - | 2 | 660T5516 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | -60 | °C | - | 180 | °C | - | - | - | - | - | - | AI40 | - | - | - | - | - | - | - | - | - | - | - | 660BJTS550/TS1-P03 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5517 | - | 660K5001 - MACHINE PROTECTION SYSTEM | RTD | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -60 | 180 | High Alarm (120) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 120 | - | - | - | 2 | 660T5517 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | -60 | °C | - | 180 | °C | - | - | - | - | - | - | AI40 | - | - | - | - | - | - | - | - | - | - | - | 660BJTS550/TS1-P04 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5518 | - | 660K5001 - MACHINE PROTECTION SYSTEM | RTD | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -60 | 180 | High Alarm (120) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 120 | - | - | - | 2 | 660T5518 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | -60 | °C | - | 180 | °C | - | - | - | - | - | - | AI40 | - | - | - | - | - | - | - | - | - | - | - | 660BJTS550/TS1-P05 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5519 | - | 660K5001 - MACHINE PROTECTION SYSTEM | RTD | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -60 | 180 | High Alarm (120) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 120 | - | - | - | 2 | 660T5519 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | -60 | °C | - | 180 | °C | - | - | - | - | - | - | AI40 | - | - | - | - | - | - | - | - | - | - | - | 660BJTS550/TS1-P06 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TI5513 | - | 660K5001 - MACHINE PROTECTION SYSTEM | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660T5513 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660TAH5513 | - | 660K5001 - MACHINE PROTECTION SYSTEM | HIGH TEMPERATURE ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | High Alarm (115) | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5513 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5512A | - | 660K5001 - MACHINE PROTECTION SYSTEM | THERMO DUPLEX | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -20 | 200 | High Alarm (115) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 115 | - | - | - | 2 | 660T5512 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | -20 | °C | - | 200 | °C | - | - | - | - | - | - | AI40 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJTS550/TS2-P05 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TE5512B | - | 660K5001 - MACHINE PROTECTION SYSTEM | THERMO DUPLEX | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -20 | 200 | High Alarm (115) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 115 | - | - | - | 2 | 660T5512 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | -20 | °C | - | 200 | °C | - | - | - | - | - | - | AI40 | - | - | - | - | - | - | - | - | - | - | - | 660BJTS550/TS2-P06 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660TE5512C | - | 660K5001 - MACHINE PROTECTION SYSTEM | THERMO DUPLEX | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -20 | 200 | High Alarm (115) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5512 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI40 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJTS550/TS2-P07 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660TE5512D | - | 660K5001 - MACHINE PROTECTION SYSTEM | THERMO DUPLEX | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -20 | 200 | High Alarm (115) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5512 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI40 | - | - | - | - | - | - | - | - | - | - | - | 660BJTS550/TS2-P08 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TE5513A | - | 660K5001 - MACHINE PROTECTION SYSTEM | THERMO DUPLEX | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -20 | 200 | High Alarm (115) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 115 | - | - | - | 2 | 660T5513 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | -20 | °C | - | 200 | °C | - | - | - | - | - | - | AI40 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJTS550/TS2-P01 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TE5513B | - | 660K5001 - MACHINE PROTECTION SYSTEM | THERMO DUPLEX | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -20 | 200 | High Alarm (115) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 115 | - | - | - | 2 | 660T5513 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | -20 | °C | - | 200 | °C | - | - | - | - | - | - | AI40 | - | - | - | - | - | - | - | - | - | - | - | 660BJTS550/TS2-P02 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660TE5513C | - | 660K5001 - MACHINE PROTECTION SYSTEM | THERMO DUPLEX | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -20 | 200 | High Alarm (115) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5513 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI40 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJTS550/TS2-P03 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660TE5513D | - | 660K5001 - MACHINE PROTECTION SYSTEM | THERMO DUPLEX | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -20 | 200 | High Alarm (115) | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5513 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI40 | - | - | - | - | - | - | - | - | - | - | - | 660BJTS550/TS2-P04 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TG5550 | - | Inlet water temperature Lube oil coolers 660-E-5009A | THERMOMETER | - | - | - | - | - | L | - |  | - | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5550 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | HOLD | - | - | - | - | - | - | - | - | - | -10 | °C | - | 60 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TG5551 | - | 660 K 5001 COMPRESSOR | THERMOMETER | - | - | - | N | - | L | - | - | - | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5551 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | -10 | °C | - | 60 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TG5552 | - | 660 K 5001 COMPRESSOR | THERMOMETER | - | - | - | N | - | L | - | - | - | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5552 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | -10 | °C | - | 60 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TG5553 | - | 660 K 5001 COMPRESSOR | THERMOMETER | - | - | - | N | - | L | - | - | - | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5553 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | -10 | °C | - | 60 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TCV5554 | - | 660 K 5001 COMPRESSOR | TEMPERATURE REGULATOR | - | - | - | N | - | L | - | - | - | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660T5554 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TAH5555 | - | 660 K 5001 COMPRESSOR | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | High Alarm (65) | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5555 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TE5555 | - | 660 K 5001 COMPRESSOR | RTD | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660T5555 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-4"-P-2008.0-3BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TIC5555 | - | 660 K 5001 COMPRESSOR | TEMPERATURE INDICATING CONTROLLER | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | Alarm H: 65 Alarm L: 10 | - | - | - | 4 | 660T5555 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TT5577 | - | 660 K 5001 COMPRESSOR | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -20 | 140 | High Alaam (65 °C) | °C | P22201-100-02 | - | - | - | - | 660-2-Fractionation | Alarm H: 60 | - | - | - | 3 | 660T5577 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | - | HOLD | HOLD | - | - | - | - | - | - | - | - | - | -20 | °C | - | 140 | °C | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM515/P07 | - | - | - | - | - | - | - | - | - | - | - | 660-4"-P-2008.0-3BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660TW5555 | - | 660 K 5001 COMPRESSOR | THERMOWELL | - | - | - | N | - | L | - | BPCS | - | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660T5555 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-4"-P-2008.0-3BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660TAL5555 | - | 660 K 5001 COMPRESSOR | LOW-TEMPERATURE ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | Low Alaam (10°C) | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660T5555 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TSHH5556 | 660-TS -5556 | 660 K 5001 COMPRESSOR | TEMPERATURE SWITCH | - | - | - | N | - | L | ST1C | BPCS | DCS | - | - | - | High High Alarm (80°C) | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660T5556 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | - | HOLD | HOLD | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660BJT505/P02 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TZA5556 | - | 660 K 5001 COMPRESSOR | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | Alarm HH: 80 | - | - | - | 8 | 660T5556 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660TS5556 | - | Temperature control Lube oil E-heater 660-F-5002 | TEMPERATURE SWITCH | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660T5556 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | °C | - | 100 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PDT5580 | - | HOLD | DIFFERENTIAL PRESSURE TRANSMITTER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 25 | 5000 | - | mbar | P22201-100-02 | - | - | - | - | 660-2-Fractionation | Alarm L: 0.13 mbar | - | - | - | 3 | 660P5580 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | - | - | - | - | - | - | - | - | - | - | - | - | 1 | mbar | - | 50 | mbar | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM515/P08 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660TSH5578 | - | Temperature control Lube oil E-heater 660-F-5002 | TEMPERATURE SWITCH | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660T5578 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | - | HOLD | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | - | - | - | - | - | - | - | - | - | - | - | 660BJT505/P01 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660TS5578 | - | Temperature control Lube oil E-heater 660-F-5002 | TEMPERATURE SWITCH | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | Alarm H: 70 | - | - | - | 7 | 660T5578 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | °C | - | 100 | °C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV15 | - | 1 | - | 1 | - | 660HLS5001 | - | 660UVS5001 | TPL OPEN / CLOSE | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660U5001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV15 | - | 2 | - | 1 | - | 660HS5001 | - | 660UVS5001 SOFT RESET | PB SOFT | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV15 | - | 3 | - | 1 | - | 660UVS5001 | - | FRACTIONATOR OFFGAS COMPRESSOR SUCTION | ON OFF VALVE | - | - | - | - | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA019D | CI9/CI10 | P | LP | TV3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-14"-P-2028.0-1BB1 | OTHER | OTHER | - | 4 | - | 160 | - | - | - | - | Annex III Module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UVS -5001-SP
- | - | UV15 | - | 8 | - | 1 | - | 660UYS5002F | - | On-ff Valve 660UVS5002 | AIR SOLENOID SPRING | - | - | SOLENOID ONLY | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5002 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS503/C05-C06 | - | E10207 | 660IADM112/02 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5002F-SP
- | - | UV07 | - | 4 | - | 1 | - | 660UZSH5055 | 660UZH1055 | 660-UVS-5055 OPEN | LIMIT SWITCH | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0216 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5055 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS502/P10 | - | With UZSL | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 3 | - | 1 | - | 660UZSH5119 | - | PROCCES FLUID FROM 660 K 5001 | LIMIT SWITCH | - | - | - | N | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5119 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS502/P11 | - | With UZSL | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV15 | - | 7 | - | 1 | - | 660XA5001 | - | 660UVS5001 DISC | ALARM | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV15 | - | 4 | - | 1 | - | 660UYS5002O | - | 660-UVS-5002 | AIR SOLENOID SPRING | - | - | SOLENOID ONLY | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5002 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS503/C07-C08 | - | E10207 | 660IADM112/02 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5002-SP
- | - | UV15 | - | 6 | - | 1 | - | 660UZSL5001 | - | 660-UVS-5001 CLOSE | LIMIT SWITCH | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | Alarm H: Open | - | - | - | 7 | 660U5001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS502/P12 | - | E10205 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV15 | - | 10 | - | 1 | - | 660HS5001B | - | 660-UVS-5001 CLOSE | ESD PB | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5001 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PT5387 | - | API PLAN PUMP 660G5003A | PRESSURE TRANSMITTER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -1 | 5 | - | barG | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5387 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM533/P08 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV15 | - | 12 | - | 1 | - | 660PI5001 | - | 660UVS5001 AIR RESERVE | PRESSURE INDICATOR | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660U5001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | LP | TV | - | - | - | - | - | - | - | - | - | bar | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | OTHER | OTHER | 6.3 | 9 | 40 | 70 | - | - | - | - | General Note 17 | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PI -5001-SP
- | - | UV15 | - | 13 | - | 1 | - | 660PAL5001 | - | 660UVS5001 AIR RESERVE | ALARM | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - | - | - | 4 | Bar | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | LP | TV | - | - | - | - | - | - | - | - | - | bar | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | OTHER | OTHER | 6.3 | 9 | 40 | 70 | - | - | - | - | General Note 17 | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PAL -5001-SP
- | - | UV15 | - | 14 | - | 1 | - | 660PSV5001 | - | 660D5011 AIR RESERVE (ACCU) 660UVS5001 | PRESSURE RELIEF VALVE | - | - | - | - | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI2 | P | LP | TV | - | - | - | - | - | - | - | - | - | bar | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ACCU | - | - | - | - | - | - | - | - | - | - | General Note 17 | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | UV15 | - | 1 | - | 1 | - | 660HLS5002 | - | 660UVS5002 | TPL OPEN / CLOSE | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660U5002 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV15 | - | 2 | - | 1 | - | 660HS5002 | - | 660UVS5002 SOFT RESET | PB SOFT | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5002 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV15 | - | 3 | - | 1 | - | 660UVS5002 | - | FRACTIONATOR OFF GAS COMRPESSOR DISCHARGE | ON OFF VALVE | - | - | - | - | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5002 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA019D | CI9 | NO | - | PP | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2035.0-1BB1 | OTHER | OTHER | - | 8.5 | - | 200 | - | - | - | - | Annex III Module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UVS -5002-SP
- | - | UV05 | - | 3 | - | 1 | - | 660UYS5014 | - | On-ff Valve 660UVS5014 | AIR SOLENOID SPRING | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5014 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS503/C09-C10 | - | E10207 | 660IADM518/07 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5014-SP
- | - | UV15 | - | 6 | - | 1 | - | 660UZSL5002 | - | 660-UVS-5002 CLOSE | LIMIT SWITCH | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | Alarm H: Open | - | - | - | 7 | 660U5002 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS502/P13 | - | E10205 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 5 | - | 1 | - | 660UZSL5014 | - | 660-UVS-5014 CLOSE | LIMIT SWITCH | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5014 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS502/P14 | - | E10205 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV15 | - | 7 | - | 1 | - | 660XA5002 | - | 660UVS5002 DISC | ALARM | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5002 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV07 | - | 3 | - | 1 | - | 660UYS5055 | 660UYS1055 | On-ff Valve 660UVS5055 | AIR SOLENOID SPRING | - | - | SOLENOID ONLY | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0216 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5055 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS503/C11-C12 | - | E10207 | 660IADM517/04 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5055-SP
- | - | UV07 | - | 5 | - | 1 | - | 660UZSL5055 | 660UZSL1055 | 660-UVS-5055 CLOSE | LIMIT SWITCH | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0216 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5055 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS502/P15 | - | E10205 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV15 | - | 10 | - | 1 | - | 660HS5002B | - | 660-UVS-5002 CLOSE | ESD PB | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5002 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660PT5388 | - | API PLAN PUMP 660G5003B | PRESSURE TRANSMITTER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -1 | 5 | - | barG | FR-GPS-100-0-FLOW-002121 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660P5388 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY VENDOR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM533/P09 | - | E10201 | - | - | - | - | - | - | - | - | - | E. | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV15 | - | 12 | - | 1 | - | 660PI5002 | - | 660UVS5002 AIR RESERVE | PRESSURE INDICATOR | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660U5002 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | LP | TV | - | - | - | - | - | - | - | - | - | bar | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | OTHER | OTHER | 6.3 | 9 | 40 | 70 | - | - | - | - | General Note 17 | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PI -5002-SP
- | - | UV15 | - | 13 | - | 1 | - | 660PAL5002 | - | 660UVS5002 AIR RESERVE | ALARM | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - |  |  | 4 | Bar | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5002 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | LP | TV | - | - | - | - | - | - | - | - | - | bar | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | OTHER | OTHER | 6.3 | 9 | 40 | 70 | - | - | - | - | General Note 17 | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-PAL -5002-SP
- | - | UV15 | - | 14 | - | 1 | - | 660PSV5002 | - | 660D5012 AIR RESERVE (ACCU) 660UVS5002 | PRESSURE RELIEF VALVE | - | - | - | - | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5002 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI2 | P | LP | TV | - | - | - | - | - | - | - | - | - | bar | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ACCU | - | - | - | - | - | - | - | - | - | - | General Note 17 | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | UV03 | - | 1 | - | 1 | - | 660HLS5003 | - | 660-UV-5003 | TPL OPEN / CLOSE | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0209 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660U5003 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV03 | - | 2 | - | 1 | - | 660UV5003 | - | 660-UV-5003 | ON OFF VALVE | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0209 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5003 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | - | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-4"-P-2026.0-3BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV03 | - | 3 | - | 1 | - | 660UY5003 | - | 660-UV-5003 | SOLENOID SPRING | - | - | WITH ON OFF VALVE | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0209 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5003 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV03 | - | 4 | - | 1 | - | 660UZSH5003 | - | 660-UV-5003 OPEN | LIMIT SWITCH | - | - | INDUCTIVE | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0209 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5003 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV03 | - | 5 | - | 1 | - | 660UZSL5003 | - | 660-UV-5003 CLOSE | LIMIT SWITCH | - | - | INDUCTIVE | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0209 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5003 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV03 | - | 6 | - | 1 | - | 660XA5003 | - | 660-UV-5003 DISC | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0209 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5003 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV03 | - | 1 | - | 1 | - | 660HLS5004 | - | 660-UV-5004 | TPL OPEN / CLOSE | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0209 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660U5004 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV03 | - | 2 | - | 1 | - | 660UV5004 | - | 660-UV-5004 | ON OFF VALVE | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0209 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5004 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1 | - | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-4"-P-2026.1-3BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV03 | - | 3 | - | 1 | - | 660UY5004 | - | 660-UV-5004 | SOLENOID SPRING | - | - | WITH ON OFF VALVE | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0209 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5004 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV03 | - | 4 | - | 1 | - | 660UZSH5004 | - | 660-UV-5004 OPEN | LIMIT SWITCH | - | - | INDUCTIVE | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0209 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5004 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV03 | - | 5 | - | 1 | - | 660UZSL5004 | - | 660-UV-5004 CLOSE | LIMIT SWITCH | - | - | INDUCTIVE | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0209 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5004 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV03 | - | 6 | - | 1 | - | 660XA5004 | - | 660-UV-5004 DISC | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0209 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5004 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV13 | - | 1 | - | 1 | - | 660HLS5006 | - | 660UV5006 | TPL OPEN / CLOSE | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660U5006 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV13 | - | 2 | - | 1 | - | 660UV5006 | - | BIODIESEL PRODUCT TO BATTERY LIMIT | ON OFF VALVE | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5006 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA008 | CI9/CI10 | P | LP | TV3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660IADM512/05 | - | - | - | - | - | - | - | - | 660-4"-P-2008.0-3BB1 | OTHER | L | - | 19 | - | 260 | - | - | - | - | Annex III Module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UV -5006-SP
- | - | UV13 | - | 3 | - | 1 | - | 660UY5006O | - | 660-UV-5006 | AIR SOLENOID SPRING | - | - | WITH ON OFF VALVE | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5006 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJC500/C01-C02 | - | E10207 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UY -5006O-SP
- | - | UV13 | - | 4 | - | 1 | - | 660UZSH5568 | - | OFF SPEC NAPHTHA TO 660D5001 | LIMIT SWITCH | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0041-0001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5568 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM500/P05 | - | With UZSL | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV13 | - | 5 | - | 1 | - | 660UZSL5568 | - | OFF SPEC NAPHTHA TO 660D5001 | LIMIT SWITCH | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0041-0001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660U5568 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJM500/P06 | - | E10205 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV13 | - | 6 | - | 1 | - | 660XA5006 | - | 660UV5006 DISC | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5006 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV13 | - | 3 | - | 1 | - | 660UY5007O | - | 660-UV-5007 | AIR SOLENOID SPRING | - | - | WITH ON OFF VALVE | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5007 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJC500/C03-C04 | - | E10207 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UY -5007O-SP
- | - | UV13 | - | 1 | - | 1 | - | 660HLS5007 | - | 660UV5007 | TPL OPEN / CLOSE | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660U5007 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV13 | - | 2 | - | 1 | - | 660UV5007 | - | BIODIESEL TO OFF SPEC TANK | ON OFF VALVE | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5007 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA008 | CI9/CI10 | P | LP | TV3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660IADM512/06 | - | - | - | - | - | - | - | - | 660-4"-P-2008.1-3BB1 | OTHER | L | - | 19 | - | 260 | - | - | - | - | Annex III Module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UV -5007-SP
- | - | UV13 | - | 7 | - | 1 | - | 660UY5006F | - | 660-UV-5006 | AIR SOLENOID SPRING | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5006 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJC500/C05-C06 | - | E10207 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UY -5006F-SP
- | - | - | - | 1 | - | 1 | - | 660HZSL5401 | - | SWITCH VALVE FOR POSITION BURNER FLAME LOST | LIMIT SWITCH | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660H5401 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM500/P07 | - | E10204 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HZSL5402 | - | SWITCH VALVE FOR POSITION BURNER FLAME LOST | LIMIT SWITCH | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660H5402 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM500/P08 | - | E10204 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV13 | - | 6 | - | 1 | - | 660XA5007 | - | 660UV5007 DISC | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5007 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV13 | - | 7 | - | 1 | - | 660UY5007F | - | 660-UV-5007 | AIR SOLENOID SPRING | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5007 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJC500/C07-C08 | - | E10207 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UY -5007F-SP
- | - | UV05 | - | 1 | - | 1 | - | 660HLS5011 | - | 660UV5011 | TPL OPEN / CLOSE | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660U5011 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 2 | - | 1 | - | 660UVS5011 | - | PRODUCT FRACTIONATOR BOTTOMS | ON OFF VALVE | - | - | - | - | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5011 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA007 | CI9 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-18"-P-2006.0-3BB3 | OTHER | L | - | 5.2 | - | 390 | - | - | - | - | Annex III Module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UVS -5011-SP
- | - | UV12 | - | 3 | - | 1 | - | 660UYS5306A | - | On-ff Valve 660UVS5306 | AIR SOLENOID SPRING | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5306 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS500/C05-C06 | - | E10207 | 660IADM514/03 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5306A-SP
- | - | UV14 | - | 7 | - | 1 | - | 660HS5012 | 660-HS -5012A | 660-UVS-5012 | PB SOFT | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5012 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS501/P03 | - | E10204 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 4 | - | 1 | - | 660UZSH5011 | - | 660-UV-5011 OPEN | LIMIT SWITCH | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5011 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS501/P05 | - | With UZSL | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 6 | - | 1 | - | 660XA5011 | - | 660UV5011 DISC | ALARM | - | - | - | N | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5011 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV14 | - | 4 | - | 1 | - | 660UZSH5012 | - | 660-UVS-5012 OPEN | LIMIT SWITCH | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5012 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS501/P06 | - | With UZSL | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 8 | - | 1 | - | 660HS5011B | - | 660-UV-5011 | ESD PB | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5011 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV14 | - | 1 | - | 1 | - | 660HLS5012 | - | 660UVS5012 | TPL OPEN / CLOSE | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5012 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV14 | - | 2 | - | 1 | - | 660UVS5012 | - | PRODUCT FRACTIONATOR REBOILER INLET | ON OFF VALVE | - | - | - | - | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5012 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA007D | CI9 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-10"-P-2009.1-3BB3 | OTHER | L | - | 19 | - | 390 | - | - | - | - | Annex III Module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UVS -5012-SP
- | - | UV12 | - | 8 | - | 1 | - | 660UYS5305B | - | 660-UVS-5305 | AIR SOLENOID SPRING | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5305 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS500/C07-C08 | - | E10207 | 660IADM514/04 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5305B-SP
- | - | UV12 | - | 4 | - | 1 | - | 660UZSH5301 | - | 660-UVS-5301 OPEN | LIMIT SWITCH | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5301 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS501/P07 | - | With UZSL | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV12 | - | 4 | - | 1 | - | 660UZSH5302 | - | 660-UVS-5302 OPEN | LIMIT SWITCH | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5302 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS501/P08 | - | With UZSL | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV14 | - | 6 | - | 1 | - | 660XA5012 | - | 660UVS5012 | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5012 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV12 | - | 4 | - | 1 | - | 660UZSH5305 | - | 660-UVS-5305 OPEN | LIMIT SWITCH | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5305 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS501/P09 | - | With UZSL | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV14 | - | 8 | - | 1 | - | 660HS5012B | - | 660-UVS-5012 | PB SOFT | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5012 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV12 | - | 8 | - | 1 | - | 660UYS5306B | - | 660-UVS-5306 | AIR SOLENOID SPRING | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5306 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS500/C09-C10 | - | E10207 | 660IADM514/03 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5306B-SP
- | - | UV05 | - | 1 | - | 1 | - | 660HLS5013 | - | 660UV5013 | TPL OPEN / CLOSE | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5013 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 2 | - | 1 | - | 660UVS5013 | - | KEROSENE STRIPPER BOTTOMS | ON OFF VALVE | - | - | - | - | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5013 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA007 | CI9 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2013.1-3BB3 | KERO | L | - | 19 | - | 280 | - | - | - | - | Annex III Module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UVS -5013-SP
- | - | UV05 | - | 3 | - | 1 | - | 660UYS5011 | - | On-ff Valve 660UVS5011 | AIR SOLENOID SPRING | - | - | WITH ON OFF VALVE | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5011 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS500/C11-C12 | - | E10207 | 660IADM515/07 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5011-SP
- | - | UV07 | - | 6 | - | 1 | - | 660UZSL5056 | - | 660-UVS-5056 CLOSE | LIMIT SWITCH | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5056 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS500/P08 | - | E10205 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 4 | - | 1 | - | 660UZSL5150 | - | PROCCES FLUID TO FT 5154/5155 | LIMIT SWITCH | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5150 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS500/P09 | - | E10205 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 6 | - | 1 | - | 660XA5013 | - | 660UV5013 DISC | ALARM | - | - | - | N | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5013 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV07 | - | 4 | - | 1 | - | 660UZSL5291 | - | DIESEL MODE FROM 660 E 5008 | LIMIT SWITCH | - | - | - | N | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5291 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS500/P10 | - | E10205 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 8 | - | 1 | - | 660HS5013B | - | 660-UV-5013 | PB SOFT | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5013 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 1 | - | 1 | - | 660HLS5014 | - | 660UVS5014 | TPL OPEN / CLOSE | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5014 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 2 | - | 1 | - | 660UVS5014 | - | PRODUCT FRACTIONATOR RECEIVER ISOLATION | ON OFF VALVE | - | - | - | - | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5014 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA007 | CI9 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-10"-P-2027.0-1BB1 | OTHER | L | - | 4.5 | - | 120 | - | - | - | - | Annex III Module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UVS -5014-SP
- | - | UV05 | - | 2 | - | 1 | - | 660UYS5119 | - | PROCCES FLUID FROM 660 K 5001 | AIR SOLENOID SPRING | - | - | - | N | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5119 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS503/C13-C14 | - | E10207 | 660IADM518/08 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5119-SP
- | - | UV05 | - | 4 | - | 1 | - | 660UZSL5119 | - | PROCCES FLUID FROM 660 K 5001 | LIMIT SWITCH | - | - | - | N | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5119 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS502/P16 | - | E10205 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660HS5501 | - | COMRESSOR PB/ESD 660 K 5001 | ESD PB | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660H5501 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS502/P17 | - | E10204 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 6 | - | 1 | - | 660XA5014 | - | 660UVS5014 DISC | ALARM | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5014 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 16 | - | 1 | - | 660HSE5006A | - | 660-EM-5006A LOCAL ESD | ESD PB | - | - | - | N | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5006A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660BJMS502/P18 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 8 | - | 1 | - | 660HS5014B | - | 660-UVS-5014 | ESD PB | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5014 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 2 | - | 1 | - | 660UVS5015 | - | HOLD | ON OFF VALVE | - | - | - | - | - | L | - | BPCS/SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5015 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | CI1/CI9 | - | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-10"-P-2027.0-1BB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | UV05 | - | 3 | - | 1 | - | 660UYS5015 | - | HOLD | AIR SOLENOID SPRING | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5015 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 4 | - | 1 | - | 660UZSH5015 | - | HOLD | LIMIT SWITCH | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5015 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | With UZSL | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 5 | - | 1 | - | 660UZSL5015 | - | HOLD | LIMIT SWITCH | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5015 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 6 | - | 1 | - | 660HLS5015 | - | HOLD | TPL OPEN / CLOSE | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5015 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 7 | - | 1 | - | 660XA5015 | - | HOLD | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5015 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 8 | - | 1 | - | 660HS5015A | 660-HS -5015 | HOLD | PB SOFT | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5015 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 9 | - | 1 | - | 660HS5015B | - | HOLD | PB SOFT | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5015 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV07 | - | 1 | - | 1 | - | 660HLS5054 | - | 660UVS5054 | TPL OPEN / CLOSE | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660U5054 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV07 | - | 2 | - | 1 | - | 660UVS5054 | 660UVS1054 | NAPHTHA TO STORAGE | ON OFF VALVE | - | - | - | - | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5054 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA007 | CI9 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-6"-P-2087.0-1BB1 | OTHER | L | - | 11.5 | - | 122 | - | - | - | - | Annex III Module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UVS -5054-SP
- | - | UV07 | - | 3 | - | 1 | - | 660UYS5054 | 660UYS1054 | On-ff Valve 660UVS5054 | AIR SOLENOID SPRING | - | - | SOLENOID ONLY | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5054 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS504/C01-C02 | - | E10207 | 660IADM516/05 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5054-SP
- | - | UV07 | - | 4 | - | 1 | - | 660UZSH5054 | 660UZSH1054 | 660-UVS-5054 OPEN | LIMIT SWITCH | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5054 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS503/P01 | - | With UZSL | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV07 | - | 5 | - | 1 | - | 660UZSL5054 | 660UZSL1054 | 660-UVS-5054 CLOSE | LIMIT SWITCH | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5054 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS503/P02 | - | E10205 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV07 | - | 6 | - | 1 | - | 660XA5054 | - | 660UVS5054 DISC | ALARM | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5054 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV07 | - | 7 | - | 1 | - | 660HS5054 | - | 660UVS5054 SOFT RESET | PB | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5054 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV07 | - | 1 | - | 1 | - | 660HLS5055 | - | 660UVS5055 | TPL OPEN / CLOSE | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0216 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660U5055 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV07 | - | 2 | - | 1 | - | 660UVS5055 | 660UVS1055 | DEBUTANIZER REBOILER TUBE SIDE INLET | ON OFF VALVE | - | - | - | - | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0216 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5055 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA007 | CI9 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-4"-P-2016.1-3BB3 | KERO | L | - | 19 | - | 280 | - | - | - | - | Annex III Module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UVS -5055-SP
- | - | UV05 | - | 2 | - | 1 | - | 660UYS5150 | - | PROCCES FLUID TO FT 5154/5155 | AIR SOLENOID SPRING | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5150 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS503/C15-C16 | - | E10207 | 660IADM513/06 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5150-SP
- | - | MCC21 | - | 11 | - | 1 | - | 660HSE5006B | - | 660-EM-5006B LOCAL ESD | ESD PB | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5006B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS502/P19 | - | E10204 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 16 | - | 1 | - | 660HSE5006C | - | 660-EM-5006C LOCAL ESD | ESD PB | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5006C | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660BJMS502/P20 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV07 | - | 6 | - | 1 | - | 660XA5055 | - | 660UVS5055 DISC | ALARM | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0216 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5055 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV07 | - | 7 | - | 1 | - | 660HS5055 | - | 660UVS5055 SOFT RESET | PB SOFT | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0216 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5055 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV07 | - | 1 | - | 1 | - | 660HLS5056 | - | 660UVS5056 | TPL OPEN / CLOSE | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660U5056 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV07 | - | 2 | - | 1 | - | 660HS5056 | - | 660UVS5056 SOFT RESET | PB SOFT | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5056 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV07 | - | 3 | - | 1 | - | 660UVS5056 | - | FRACTIONATOR OFF GAS KNOCKOUT DRUM OUTLET | ON OFF VALVE | - | - | - | - | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5056 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA007 | CI9 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-3"-P-2041.0-1BB1 | OTHER | L | - | 8.2 | - | 180 | - | - | - | - | Annex III Module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UVS -5056-SP
- | - | UV14 | - | 3 | - | 1 | - | 660UYS5012O | 660-UYS -5012 | 660-UVS-5012 (OPEN) | AIR SOLENOID SPRING | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5012 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS500/C13-C14 | - | E10207 | 660IADM518/06 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5012-SP
- | - | MCC22 | - | 15 | - | 1 | - | 660XTS5102A | - | 660-EM-5002B VIBRATION | VIBRATION | - | - | - | N | - | L | ST1D | BPCS/SIS | S-PLC | - | 0 | 25.4 | - | mm.s | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660EM5002A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS5002/P01 | - | E10201 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 15 | - | 1 | - | 660XTS5102B | - | 660-EM-5002B VIBRATION | VIBRATION | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | 0 | 25.4 | - | mm.s | 214359C-6602-PID-0021-0206 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660EM5002B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS5002/P02 | - | E10201 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV07 | - | 7 | - | 1 | - | 660XA5056 | - | 660UVS5056 DISC | ALARM | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0213 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5056 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 1 | - | 1 | - | 660UVS5119 | - | PROCCES FLUID FROM 660 K 5001 | ON OFF VALVE | - | - | - | - | - | L | - | BPCS/SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5119 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA007 | CI9 | NO | - | PP | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-2"-P-2306.0-1BB1 | OTHER | OTHER | - | 8.5 | - | 200 | - | - | - | - | Annex III Module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UVS -5119-SP
- | - | CV04 |  | 5 |  | 2 |  | 660UYS5154 | - | NAPHTHA TO 660 C 0001 (DIESEL MODE) | AIR SOLENOID SPRING |  |  | - | - |  | L | ST1D | BPCS/SIS | S-PLC | [5 empty] | 214359C-6602-PID-0021-0211 |  |  |  |  | 660-2-Fractionation | - |  | - |  | 9 | 660F5154 | N | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [7 empty] | - | CI9/CI10 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [5 empty] | DO10 | INT | [10 empty] | 660BJCS503/C17-C18 |  | E10207 |  | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 11 | - | 1 | - | 660HSE5006D | - | 660-EM-5006C LOCAL ESD | ESD PB | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660EM5006D | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS502/P21 | - | E10204 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 2 | - | 1 | - | 660HSE0004ABB | - | 660-E-0004BB LOCAL ESD B | ESD PB | - | - | NORMALLY CLOSE | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660EM0004AB | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJMS502/P22 | - | E10204 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 5 | - | 1 | - | 660HLS5119 | - | 660UVS5119 | TPL OPEN / CLOSE | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5119 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 6 | - | 1 | - | 660XA5119 | - | 660UVS5119 DISC | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5119 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 7 | - | 1 | - | 660HS5119 | - | 660UVS5119 SOFT RESET | PB SOFT | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5119 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 6 | - | 1 | - | 660HLS5150 | - | 660UVS5150 | TPL OPEN / CLOSE | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5150 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 1 | - | 1 | - | 660UVS5150 | - | PROCCES FLUID TO FT 5154/5155 | ON OFF VALVE | - | - | - | - | - | L | - | BPCS/SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5150 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA007 | CI9 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-2"-P-2032.3-1BB1 | OTHER | OTHER | - | 12.5 | - | 120 | - | - | - | - | Annex III Module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UVS -5150-SP
- | - | CV04 |  | 6 |  | 2 |  | 660UYS5155 | - | NAPHTHA TO 660 C 0001 (JET MODE) | AIR SOLENOID SPRING |  |  | - | - |  | L | ST1D | BPCS/SIS | S-PLC | [5 empty] | 214359C-6602-PID-0021-0211 |  |  |  |  | 660-2-Fractionation | - |  | - |  | 9 | 660F5155 | N | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [7 empty] | - | CI9/CI10 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [5 empty] | DO10 | INT | [10 empty] | 660BJCS503/C19-C20 |  | E10207 |  | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC22 | - | 15 | - | 1 | - | 660XTS5006A | - | 660-EM-5006A VIBRATION | VIBRATION | - | - | - | N | - | L | ST1D | BPCS/SIS | S-PLC | - | 0 | 25.4 | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660EM5006A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS5006/P01 | - | E10201 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 10 | - | 1 | - | 660XTS5006B | - | 660-EM-5006B VIBRATION | VIBRATION | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | 0 | 25.4 | - | - | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660EM5006B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS5006/P02 | - | E10201 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 5 | - | 1 | - | 660XA5150 | - | 660UVS5150 DISC | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0211 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5150 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV07 | - | 1 | - | 1 | - | 660UVS5291 | - | DIESEL MODE FROM 660 E 5008 | ON OFF VALVE | - | - | - | - | - | L | - | BPCS/SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5291 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA007 | CI9 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-3"-P-2022.0-3BB1 | OTHER | L | - | 19 | - | 250 | - | - | - | - | Annex III Module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UVS -5291-SP
- | - | UV05 | - | 3 | - | 1 | - | 660UYS5013 | - | On-ff Valve 660UVS5013 | AIR SOLENOID SPRING | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0207 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5013 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS500/C15-C16 | - | E10207 | 660IADM515/08 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5013-SP
- | - | MCC22 | - | 15 | - | 1 | - | 660XTS5006C | - | 660-EM-5006C VIBRATION | VIBRATION | - | - | - | N | - | L | ST1D | BPCS/SIS | S-PLC | - | 0 | 25.4 | - | mm.s | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660EM5006C | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS5006/P03 | - | E10201 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC21 | - | 10 | - | 1 | - | 660XTS5006D | - | 660-EM-5006C VIBRATION | VIBRATION | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | 0 | 25.4 | - | mm.s | 214359C-6602-PID-0021-0210 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660EM5006D | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS5006/P04 | - | E10201 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV07 | - | 5 | - | 1 | - | 660XA5291 | - | 660UVS5291 DISC | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5291 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV07 | - | 6 | - | 1 | - | 660HLS5291 | - | 660UVS5291 OPEN/CLOSE | TPL OPEN / CLOSE | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660U5291 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV07 | - | 7 | - | 1 | - | 660HS5291 | - | 660UVS5291 SOFT RESET | PB SOFT | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5291 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV07 | - | 1 | - | 1 | - | 660UVS5293 | - | NAPHTHA TO OFF-SPEC STORAGE | ON OFF VALVE | - | - | - | - | - | L | - | BPCS/SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5293 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA007 | CI9 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-2"-P-2436.0-1BB1 | OTHER | L | - | 11.5 | - | 122 | - | - | - | - | Annex III Module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UVS -5293-SP
- | - | UV07 | - | 2 | - | 1 | - | 660HS5293 | - | 660UVS5293 SOFT RESET | PB | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5293 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV07 | - | 3 | - | 1 | - | 660HLS5293 | - | 660UVS5293 OPEN/CLOSE | TPL OPEN / CLOSE | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660U5293 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV07 | - | 4 | - | 1 | - | 660UYS5293 | - | NAPHTHA TO OFF-SPEC STORAGE | AIR SOLENOID SPRING | - | - | SOLENOID ONLY | N | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5293 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS504/C03-C04 | - | E10207 | 660IADM516/08 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5293-SP
- | - | UV07 | - | 5 | - | 1 | - | 660UZSH5293 | - | NAPHTHA TO OFF-SPEC STORAGE | LIMIT SWITCH | - | - | - | N | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5293 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS503/P03 | - | With UZSL | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV07 | - | 6 | - | 1 | - | 660UZSL5293 | - | NAPHTHA TO OFF-SPEC STORAGE | LIMIT SWITCH | - | - | - | N | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5293 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS503/P04 | - | E10205 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV07 | - | 7 | - | 1 | - | 660XA5293 | - | 660UVS5293 DISC | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0214 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5293 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV12 | - | 1 | - | 1 | - | 660UVS5301 | - | FUEL GAS TO F 5001 BURNERS | ON OFF VALVE | - | - | - | - | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5301 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA007 | CI9 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-4"-FG-2095.0-1KB2 | GN | OTHER | - | 3.5 | - | 75 | - | - | - | - | Annex III Module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UVS -5301-SP
- | - | UV12 | - | 3 | - | 1 | - | 660UYS5301A | - | On-ff Valve 660UVS5301 | AIR SOLENOID SPRING | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5301 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS505/C03-C04 | - | E10207 | 660IADM514/01 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5301A-SP
- | - | UV12 | - | 4 | - | 1 | - | 660UZSH5306 | - | 660-UVS-5306 OPEN | LIMIT SWITCH | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5306 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS501/P10 | - | With UZSL | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV12 | - | 5 | - | 1 | - | 660UZSH5391 | - | 660-UVS-5391 OPEN | LIMIT SWITCH | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5391 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS501/P11 | - | With UZSL | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV12 | - | 6 | - | 1 | - | 660XA5301 | - | 660UVS5301 DISC | ALARM | - | - | - | N | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5301 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV12 | - | 7 | - | 1 | - | 660HS5301 | - | 660-UVS-5301/5302/5391 | PB | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5301 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV12 | - | 8 | - | 1 | - | 660UYS5301B | - | 660-UVS-5301 | AIR SOLENOID SPRING | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5301 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS505/C05-C06 | - | E10207 | 660IADM514/01 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5301B-SP
- | - | UV12 | - | 1 | - | 1 | - | 660UVS5302 | - | FUEL GAS TO F 5001 BURNERS | ON OFF VALVE | - | - | - | - | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5302 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA007 | CI9 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-4"-FG-2095.0-1KB2 | GN | OTHER | - | 3.5 | - | 75 | - | - | - | - | Annex III Module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UVS -5302-SP
- | - | UV12 | - | 2 | - | 1 | - | 660HLS5302 | - | 660-UVS-5302 | CONTACT | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5302 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV12 | - | 3 | - | 1 | - | 660UYS5302A | - | On-ff Valve 660UVS5302 | AIR SOLENOID SPRING | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5302 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS505/C07-C08 | - | E10207 | 660IADM514/02 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5302A-SP
- | - | UV05 | - | 5 | - | 1 | - | 660UZSL5011 | - | 660-UV-5011 CLOSE | LIMIT SWITCH | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5011 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS501/P12 | - | E10205 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV14 | - | 5 | - | 1 | - | 660UZSL5012 | - | 660-UVS-5012 CLOSE | LIMIT SWITCH | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5012 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS501/P13 | - | E10205 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV12 | - | 6 | - | 1 | - | 660XA5302 | - | 660UVS5302 DISC | ALARM | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5302 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV12 | - | 8 | - | 1 | - | 660UYS5302B | - | 660-UVS-5302 | AIR SOLENOID SPRING | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5302 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS505/C09-C10 | - | E10207 | 660IADM514/02 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5302B-SP
- | - | UV12 | - | 1 | - | 1 | - | 660UVS5305 | - | FUEL GAS TO F 5001 BURNERS | ON OFF VALVE | - | - | - | - | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5305 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA007 | CI9 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-1 1/2"-FG-2095.1-1KB2 | GN | OTHER | - | 3.5 | - | 75 | - | - | - | - | Annex III Module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UVS -5305-SP
- | - | UV07 | - | 2 | - | 1 | - | 660UYS5291 | - | 660UVS5291 DIESEL MODE FROM 660 E 5008 | AIR SOLENOID SPRING | - | - | SOLENOID ONLY | N | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0203 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5291 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS500/C17-C18 | - | E10207 | 660IADM515/09 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5291-SP
- | - | UV12 | - | 5 | - | 1 | - | 660UZSL5301 | - | 660-UVS-5301 CLOSE | LIMIT SWITCH | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5301 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS501/P14 | - | E10205 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV12 | - | 5 | - | 1 | - | 660UZSL5302 | - | 660-UVS-5302 CLOSE | LIMIT SWITCH | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5302 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS501/P15 | - | E10205 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV12 | - | 6 | - | 1 | - | 660XA5305 | - | 660UVS5305 DISC | ALARM | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5305 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV14 | - | 9 | - | 1 | - | 660UYS5012F | - | On-ff Valve 660UVS5012 | AIR SOLENOID SPRING | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0204 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5012 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS500/C19-C20 | - | E10207 | 660IADM518/06 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5012F-SP
- | - | UV12 | - | 1 | - | 1 | - | 660UVS5306 | - | PILOT GAS TO F 5001 BURNERS | ON OFF VALVE | - | - | - | - | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5306 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA007 | CI9 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-1 1/2"-FG-2095.1-1KB2 | GN | OTHER | - | 3.5 | - | 75 | - | - | - | - | Annex III Module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UVS -5306-SP
- | - | UV12 | - | 2 | - | 1 | - | 660HLS5306 | - | 660-UVS-5306 | CONTACT | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5306 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | CV04 |  | 8 |  | 2 |  | 660UYS5191A | - | FROM 660 D 5002 (DIESEL MODE) | AIR SOLENOID SPRING |  |  | - | - |  | L | ST1D | BPCS/SIS | S-PLC | [5 empty] | 214359C-6602-PID-0021-0213 |  |  |  |  | 660-2-Fractionation | - |  | - |  | 9 | 660L5191 | N | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [7 empty] | - | CI9/CI10 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [5 empty] | DO10 | INT | [10 empty] | 660BJCS500/C21-C22 |  | E10207 |  | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV12 | - | 5 | - | 1 | - | 660UZSL5305 | - | 660-UVS-5305 CLOSE | LIMIT SWITCH | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5305 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS501/P16 | - | E10205 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV12 | - | 5 | - | 1 | - | 660UZSL5306 | - | 660-UVS-5306 CLOSE | LIMIT SWITCH | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5306 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS501/P17 | - | E10205 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV12 | - | 6 | - | 1 | - | 660XA5306 | - | 660UVS5306 DISC | ALARM | - | - | - | N | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5306 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV12 | - | 7 | - | 1 | - | 660HS5306 | - | 660-UVS-5306 | PB | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5306 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | CV04 |  | 9 |  | 2 |  | 660UYS5191B | - | 660 D 5002 (JET MODE) | AIR SOLENOID SPRING |  |  | - | - |  | L | ST1D | BPCS/SIS | S-PLC | [5 empty] | 214359C-6602-PID-0021-0213 |  |  |  |  | 660-2-Fractionation | - |  | - |  | 9 | 660L5191 | N | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [7 empty] | - | CI9/CI10 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [5 empty] | DO10 | INT | [10 empty] | 660BJCS500/C23-C24 |  | E10207 |  | - | - | - | - | - |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 1 | - | 1 | - | 660UVS5377A | - | FUEL GAS TO F 5001 BURNER A | ON OFF VALVE | - | - | - | - | - | L | - | BPCS/SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5377A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA007 | CI9 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-2"-FG-2222.0-1KB2 | GN | OTHER | - | 3.5 | - | 75 | - | - | - | - | Annex III Module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UVS -5377A-SP
- | - | UV05 | - | 2 | - | 1 | - | 660HLS5377A | - | 660UVS5377A | TPL OPEN / CLOSE | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5377A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 3 | - | 1 | - | 660XA5377A | - | 660UVS5377A DISC | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5377A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 5 | - | 1 | - | 660UZSH5377B | - | PILOT GAS TO F 5001 BURNER A | LIMIT SWITCH | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5377B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS504/P05 | - | With UZSL | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 5 | - | 1 | - | 660UZSH5378A | - | FUEL GAS TO F 5001 BURNER B | LIMIT SWITCH | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5378A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS504/P06 | - | With UZSL | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 6 | - | 1 | - | 660UYS5377A | - | FUEL GAS TO F 5001 BURNER A | AIR SOLENOID SPRING | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5377A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS501/C03-C04 | - | E10207 | 660IADM510/01 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5377A-SP
- | - | UV05 | - | 1 | - | 1 | - | 660UVS5377B | - | PILOT GAS TO F 5001 BURNER A | ON OFF VALVE | - | - | - | - | - | L | - | BPCS/SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5377B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA007 | CI9 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-1/2"-FG-2223.0-1KB2 | GN | OTHER | - | 3.5 | - | 75 | - | - | - | - | Annex III Module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UVS -5377B-SP
- | - | UV05 | - | 2 | - | 1 | - | 660HLS5377B | - | 660UVS5377B | TPL OPEN / CLOSE | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5377B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 3 | - | 1 | - | 660XA5377B | - | 660UVS5377B DISC | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5377B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 4 | - | 1 | - | 660UYS5377B | - | PILOT GAS TO F 5001 BURNER A | AIR SOLENOID SPRING | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5377B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS501/C05-C06 | - | E10207 | 660IADM510/02 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5377B-SP
- | - | UV05 | - | 6 | - | 1 | - | 660UZSH5378B | - | PILOT GAS TO F 5001 BURNER B | LIMIT SWITCH | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5378B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS504/P07 | - | With UZSL | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 5 | - | 1 | - | 660UZSH5379A | - | FUEL GAS TO F 5001 BURNER C | LIMIT SWITCH | - | - | - | N | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5379A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS504/P08 | - | With UZSL | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 1 | - | 1 | - | 660UVS5378A | - | FUEL GAS TO F 5001 BURNER B | ON OFF VALVE | - | - | - | - | - | L | - | BPCS/SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5378A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA007 | CI9 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-2"-FG-2222.0-1KB2 | GN | OTHER | - | 3.5 | - | 75 | - | - | - | - | Annex III Module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UVS -5378A-SP
- | - | UV05 | - | 2 | - | 1 | - | 660HLS5378A | - | 660UVS5378A | TPL OPEN / CLOSE | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5378A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 3 | - | 1 | - | 660XA5378A | - | 660UVS5378A DISC | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5378A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 4 | - | 1 | - | 660UYS5378A | - | FUEL GAS TO F 5001 BURNER B | AIR SOLENOID SPRING | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5378A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS501/C07-C08 | - | E10207 | 660IADM510/03 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5378A-SP
- | - | UV05 | - | 6 | - | 1 | - | 660UZSH5379B | - | PILOT GAS TO F 5001 BURNER C | LIMIT SWITCH | - | - | - | N | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5379B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS504/P09 | - | With UZSL | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 5 | - | 1 | - | 660UZSH5380A | - | FUEL GAS TO F 5001 BURNER D | LIMIT SWITCH | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5380A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS504/P10 | - | With UZSL | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 1 | - | 1 | - | 660UVS5378B | - | PILOT GAS TO F 5001 BURNER B | ON OFF VALVE | - | - | - | - | - | L | - | BPCS/SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5378B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA007 | CI9 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-1/2"-FG-2223.0-1KB2 | GN | OTHER | - | 3.5 | - | 75 | - | - | - | - | Annex III Module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UVS -5378B-SP
- | - | UV05 | - | 6 | - | 1 | - | 660UZSH5380B | - | PILOT GAS TO F 5001 BURNER D | LIMIT SWITCH | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5380B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS504/P11 | - | With UZSL | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 3 | - | 1 | - | 660HLS5378B | - | 660UVS5378B | TPL OPEN / CLOSE | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5378B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 4 | - | 1 | - | 660XA5378B | - | 660UVS5378B DISC | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5378B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 5 | - | 1 | - | 660UYS5378B | - | PILOT GAS TO F 5001 BURNER B | AIR SOLENOID SPRING | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5378B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS501/C09-C10 | - | E10207 | 660IADM510/04 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5378B-SP
- | - | - | - | 8 | - | 1 | - | 660UZSL5308 | - | TO 660 F 5001 | LIMIT SWITCH | - | - | INDUCTIVE | - | - | L | ST1D | BPCS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0220 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660P5308 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS504/P12 | - | E10205 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 1 | - | 1 | - | 660UVS5379A | - | FUEL GAS TO F 5001 BURNER C | ON OFF VALVE | - | - | - | - | - | L | - | BPCS/SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5379A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA007 | CI9 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-2"-FG-2222.0-1KB2 | GN | OTHER | - | 3.5 | - | 75 | - | - | - | - | Annex III Module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UVS -5379A-SP
- | - | UV05 | - | 2 | - | 1 | - | 660HLS5379A | - | 660UVS5379A | TPL OPEN / CLOSE | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5379A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 3 | - | 1 | - | 660XA5379A | - | 660UVS5379A DISC | ALARM | - | - | - | N | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5379A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 4 | - | 1 | - | 660UYS5379A | - | FUEL GAS TO F 5001 BURNER C | AIR SOLENOID SPRING | - | - | - | N | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5379A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS501/C11-C12 | - | E10207 | 660IADM510/05 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5379A-SP
- | - | UV05 | - | 5 | - | 1 | - | 660UZSL5377A | - | FUEL GAS TO F 5001 BURNER A | LIMIT SWITCH | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5377A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS504/P13 | - | E10205 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 6 | - | 1 | - | 660UZSL5377B | - | PILOT GAS TO F 5001 BURNER A | LIMIT SWITCH | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5377B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS504/P14 | - | E10205 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 1 | - | 1 | - | 660UVS5379B | - | PILOT GAS TO F 5001 BURNER C | ON OFF VALVE | - | - | - | - | - | L | - | BPCS/SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5379B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA007 | CI9 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-1/2"-FG-2223.0-1KB2 | GN | OTHER | - | 3.5 | - | 75 | - | - | - | - | Annex III Module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UVS -5379B-SP
- | - | UV05 | - | 6 | - | 1 | - | 660UZSL5378A | - | FUEL GAS TO F 5001 BURNER B | LIMIT SWITCH | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5378A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS504/P15 | - | E10205 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 3 | - | 1 | - | 660HLS5379B | - | 660UVS5379B | TPL OPEN / CLOSE | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5379B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 4 | - | 1 | - | 660XA5379B | - | 660UVS5379B DISC | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5379B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 5 | - | 1 | - | 660UYS5379B | - | PILOT GAS TO F 5001 BURNER C | AIR SOLENOID SPRING | - | - | - | N | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5379B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS501/C13-C14 | - | E10207 | 660IADM510/06 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5379B-SP
- | - | UV05 | - | 2 | - | 1 | - | 660UZSL5378B | - | PILOT GAS TO F 5001 BURNER B | LIMIT SWITCH | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5378B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS504/P16 | - | E10205 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 1 | - | 1 | - | 660UVS5380A | - | FUEL GAS TO F 5001 BURNER D | ON OFF VALVE | - | - | - | - | - | L | - | BPCS/SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5380A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA007 | CI9 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-2"-FG-2222.0-1KB2 | GN | OTHER | - | 3.5 | - | 75 | - | - | - | - | Annex III Module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UVS -5380A-SP
- | - | UV05 | - | 2 | - | 1 | - | 660HLS5380A | - | 660UVS5380A | TPL OPEN / CLOSE | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5380A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 3 | - | 1 | - | 660XA5380A | - | 660UVS5380A DISC | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5380A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 4 | - | 1 | - | 660UYS5380A | - | FUEL GAS TO F 5001 BURNER D | AIR SOLENOID SPRING | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5380A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS501/C15-C16 | - | E10207 | 660IADM510/07 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5380A-SP
- | - | UV05 | - | 6 | - | 1 | - | 660UZSL5379A | - | FUEL GAS TO F 5001 BURNER C | LIMIT SWITCH | - | - | - | N | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5379A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS504/P17 | - | E10205 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 2 | - | 1 | - | 660UZSL5379B | - | PILOT GAS TO F 5001 BURNER C | LIMIT SWITCH | - | - | - | N | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5379B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS504/P18 | - | E10205 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 1 | - | 1 | - | 660UVS5380B | - | PILOT GAS TO F 5001 BURNER D | ON OFF VALVE | - | - | - | - | - | L | - | BPCS/SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5380B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA007 | CI9 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-1/2"-FG-2223.0-1KB2 | GN | OTHER | - | 3.5 | - | 75 | - | - | - | - | Annex III Module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UVS -5380B-SP
- | - | UV05 | - | 6 | - | 1 | - | 660UZSL5380A | - | FUEL GAS TO F 5001 BURNER D | LIMIT SWITCH | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5380A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS504/P19 | - | E10205 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 3 | - | 1 | - | 660HLS5380B | - | 660UVS5380B | TPL OPEN / CLOSE | - | - | - | N | - | CRD | SdC | BPCS/SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5380B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 4 | - | 1 | - | 660XA5380B | - | 660UVS5380B DISC | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5380B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 5 | - | 1 | - | 660UYS5380B | - | PILOT GAS TO F 5001 BURNER D | AIR SOLENOID SPRING | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5380B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS501/C17-C18 | - | E10207 | 660IADM510/08 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5380B-SP
- | - | UV05 | - | 2 | - | 1 | - | 660UZSL5380B | - | PILOT GAS TO F 5001 BURNER D | LIMIT SWITCH | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5380B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS504/P20 | - | E10205 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV12 | - | 1 | - | 1 | - | 660UVS5390 | - | PILOT GAS SAFE VENT | ON OFF VALVE | - | - | - | - | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5390 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA007 | CI9 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-3/4"-FG-2095.1-1KB2 | GN | OTHER | - | 3.5 | - | 75 | - | - | - | - | Annex III Module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UVS -5390-SP
- | - | UV12 | - | 2 | - | 1 | - | 660HLS5390 | - | 660-UVS-5390 | CONTACT | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5390 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV12 | - | 3 | - | 1 | - | 660UYS5390A | - | 660-UVS-5390 | AIR SOLENOID SPRING | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5390 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS505/C11-C12 | - | E10207 | 660IADM514/07 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5390A-SP
- | - | UV12 | - | 5 | - | 1 | - | 660UZSL5390 | - | 660-UVS-5390 CLOSE | LIMIT SWITCH | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5390 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS506/P04 | - | E10205 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- |  | - |  | 7 |  | 2 |  | 660FZSL5155 | - | NAPHTHA TO 660 C 0001 (JET MODE) | LIMIT SWITCH |  |  | - | - |  | L | ST1D | BPCS/SIS | S-PLC | [5 empty] | 214359C-6602-PID-0021-0211 |  |  |  |  | 660-2-Fractionation | - |  | - | - | 7 | 660F5155 | N | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [5 empty] | DI10 | INT |  |  | - | - | [6 empty] | 660BJMS506/P05 |  | E10204 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV12 | - | 6 | - | 1 | - | 660XA5390 | - | 660UVS5390 DISC | ALARM | - | - | - | N | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5390 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV12 | - | 7 | - | 1 | - | 660UYS5390B | - | 660-UVS-5390 | AIR SOLENOID SPRING | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5390 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS505/C13-C14 | - | E10207 | 660IADM514/07 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5390B-SP
- | - | UV12 | - | 1 | - | 1 | - | 660UVS5391 | - | BURNERS SAFE VENT | ON OFF VALVE | - | - | - | - | - | L | - | SIS | - | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5391 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA007 | CI9 | NO | - | CC | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-3/4"-FG-2095.0-1KB2 | GN | OTHER | - | 3.5 | - | 75 | - | - | - | - | Annex III Module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UVS -5391-SP
- | - | UV12 | - | 2 | - | 1 | - | 660UYS5391A | - | 660-UVS-5391 | AIR SOLENOID SPRING | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5391 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS505/C15-C16 | - | E10207 | 660IADM514/06 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5391A-SP
- | - | UV12 | - | 3 | - | 1 | - | 660UZSL5391 | - | 660-UVS-5391 CLOSE | LIMIT SWITCH | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5391 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJMS501/P18 | - | E10205 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV12 | - | 4 | - | 1 | - | 660HLS5391 | - | 660-UVS-5391 | CONTACT | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660U5391 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- |  | - |  | 6 |  | 2 |  | 660FZSL5154 | - | NAPHTHA TO 660 C 0001 (DIESEL MODE) | LIMIT SWITCH |  |  | - | - |  | L | ST1D | BPCS/SIS | S-PLC | [5 empty] | 214359C-6602-PID-0021-0211 |  |  |  |  | 660-2-Fractionation | - |  | - | - | 7 | 660F5154 | N | - |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [5 empty] | DI10 | INT |  |  | - | - | [6 empty] | 660BJMS501/P19 |  | E10204 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV12 | - | 6 | - | 1 | - | 660XA5391 | - | 660UVS5391 DISC | ALARM | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5391 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV12 | - | 7 | - | 1 | - | 660UYS5391B | - | 660-UVS-5391 | AIR SOLENOID SPRING | - | - | - | N | - | L | ST1D | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5391 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJCS505/C17-C18 | - | E10207 | 660IADM514/06 | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UYS -5391B-SP
- | - | UV13 | - | 1 | - | 1 | - | 660HLS5568 | - | 660UVS5568 | TPL OPEN / CLOSE | - | - | - | - | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0041-0001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660U5568 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV13 | - | 2 | - | 1 | - | 660UV5568 | - | OFF SPEC NAPHTHA TO 660D5001 | ON OFF VALVE | - | - | - | - | - | L | - | BPCS | - | - | - | - | - | - | 214359C-6602-PID-0041-0001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 10 | 660U5568 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 214359C-1000-STD-1575-0001/IA008 | CI9 | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660IADM513/07 | - | - | - | - | - | - | - | - | 660-2"-P-2437.0-1BB1 | OTHER | L | - | 11.5 | - | 122 | - | - | - | - | Annex III Module H | - | - | - | - | ATEX | 2 | IIC | T6 | - | - | - | - | - | - | - | 660-UV -5568-SP
- | - | UV13 | - | 3 | - | 1 | - | 660UY5568O | - | OFF SPEC NAPHTHA TO 660D5001 | AIR SOLENOID SPRING | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0041-0001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5568 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJC500/C09-C10 | - | E10207 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-UY -5568O-SP
- | - | - | - | 1 | - | 1 | - | 660HZSL5403 | - | SWITCH VALVE FOR POSITION BURNER FLAME LOST | LIMIT SWITCH | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660H5403 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM500/P09 | - | E10204 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660HZSL5404 | - | SWITCH VALVE FOR POSITION BURNER FLAME LOST | LIMIT SWITCH | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660H5404 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJM500/P10 | - | E10204 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | UV13 | - | 6 | - | 1 | - | 660XA5568 | - | 660UVS5568 DISC | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0041-0001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660U5568 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV13 | - | 7 | - | 1 | - | 660UY5568F | - | OFF SPEC NAPHTHA TO 660D5001 | AIR SOLENOID SPRING | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0041-0001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660U5568 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO11 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJC500/C11-C12 | - | E10207 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660-UY -5568F-SP
- | - | - | - | 1 | - | 1 | - | 660XTS0527 | - | 660G0002-RADIAL VIBRATION SENSOR (ACCELEROMETER) | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -490 | 490 | - | m/s² | FR-GPS-660-2-TENV-660G0002 MMS | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660X0527 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY MECHANICAL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJIMS533/P01 | - | E10101 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XTS0528 | - | 660G0102-RADIAL VIBRATION SENSOR (ACCELEROMETER) | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -490 | 490 | - | m/s² | FR-GPS-660-2-TENV-660G0102 MMS | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660X0528 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY MECHANICAL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJIMS534/P01 | - | E10101 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XTS0529 | - | 660G0003-RADIAL VIBRATION SENSOR (ACCELEROMETER) | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -490 | 490 | - | m/s² | FR-GPS-660-2-TENV-660G0003 MMS | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660X0529 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY MECHANICAL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJIMS533/P02 | - | E10101 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XTS0530 | - | 660G0103-RADIAL VIBRATION SENSOR (ACCELEROMETER) | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -490 | 490 | - | m/s² | FR-GPS-660-2-TENV-660G0103 MMS | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660X0530 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY MECHANICAL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJIMS534/P02 | - | E10101 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XS0560 | - | 660G0002 TRIP FROM MPS TO S-PLC | CONTACT | - | - | NORMALLY CLOSE | - | - | ITR | ST1D | MAINT | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-660G0002 MMS | - | - | - | - | 660-2-Fractionation | FROM ST1C / MMS | - | - | - | 7 | 660X0560 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | N/A | - | By OSBL | - | - | - | - | - | 24 VDC-MMS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XS0561 | - | 660G0102 TRIP FROM MPS TO S-PLC | CONTACT | - | - | NORMALLY CLOSE | - | - | ITR | ST1D | MAINT | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-660G0102 MMS | - | - | - | - | 660-2-Fractionation | FROM ST1C / MMS | - | - | - | 7 | 660X0561 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | N/A | - | By OSBL | - | - | - | - | - | 24 VDC-MMS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XS0562 | - | 660G0003 TRIP FROM MPS TO S-PLC | CONTACT | - | - | NORMALLY CLOSE | - | - | ITR | ST1D | MAINT | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-660G0003 MMS | - | - | - | - | 660-2-Fractionation | FROM ST1C / MMS | - | - | - | 7 | 660X0562 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | N/A | - | By OSBL | - | - | - | - | - | 24 VDC-MMS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XS0563 | - | 660G0103 TRIP FROM MPS TO S-PLC | CONTACT | - | - | NORMALLY CLOSE | - | - | ITR | ST1D | MAINT | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-660G0103 MMS | - | - | - | - | 660-2-Fractionation | FROM ST1C / MMS | - | - | - | 7 | 660X0563 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | N/A | - | By OSBL | - | - | - | - | - | 24 VDC-MMS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL5326 | 660-HS -5326 | 660F5001 | LIGHT | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660X5326 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS3-C01-C02 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XA5326 | - | HEATER READY TO START | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660X5326 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL5328 | - | 660F5001 | LIGHT | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660X5328 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS3-C03-C04 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XA5328 | - | LEAK TEST IN PROGRESS | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660X5328 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL5330 | - | 660F5001 | LIGHT | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660X5330 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS3-C05-C06 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XA5330 | - | LEAK TEST FAILURE | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660X5330 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL5332 | - | 660F5001 | LIGHT | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660X5332 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS3-C07-C08 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XA5332 | - | PURGE IN PROGRESS | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660X5332 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL5334 | - | 660F5001 | LIGHT | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660X5334 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS3-C09-C10 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XA5334 | - | PURGE FAILURE | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660X5334 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL5336 | - | 660F5001 | LIGHT | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660X5336 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS3-C11-C12 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XA5336 | - | PILOTS READY TO START | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660X5336 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL5338 | - | 660F5001 | LIGHT | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660X5338 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS3-C13-C14 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XA5338 | - | PILOT A FLAME ON | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660X5338 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL5340 | - | 660F5001 | FLASHING LIGHT | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660X5340 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS3-C15-C16 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XA5340 | - | PILOT B FLAME ON | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660X5340 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL5342 | - | 660F5001 | LIGHT | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660X5342 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS3-C17-C18 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XA5342 | - | PILOT C FLAME ON | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660X5342 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL5344 | - | 660F5001 | LIGHT | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660X5344 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS3-C19-C20 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XA5344 | - | PILOT D FLAME ON | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660X5344 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL5346 | - | 660F5001 | LIGHT | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660X5346 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS3-C21-C22 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XA5346 | - | BURNERS READY TO START | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660X5346 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL5348 | 660-ZL -5348 | 660F5001 | LIGHT | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660X5348 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS3-C23-C24 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XA5348 | - | BURNER A FLAME ON | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660X5348 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL5350 | - | 660F5001 | LIGHT | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660X5350 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS3-C25-C26 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XA5350 | - | BURNER B FLAME ON | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660X5350 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL5352 | - | 660F5001 | LIGHT | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660X5352 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS3-C27-C28 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XA5352 | - | BURNER C FLAME ON | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660X5352 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XA5353 | - | FD FAN FAULT | ALARM | - | - | - | N | - | CRD | SdC | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660X5353 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL5354 | - | 660F5001 | LIGHT | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660X5354 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS3-C29-C30 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XA5354 | - | BURNER D FLAME ON | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660X5354 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL5361 | - | 660F5001 | LIGHT | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660X5361 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS3-C31-C32 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XA5356 | - | HEATER RUNNING | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660X5356 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL5359 | - | 660F5001 | LIGHT | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660X5359 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS3-C33-C34 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XA5357 | - | HEATER PILOT TRIP | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660X5357 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL5362 | - | 660F5001 | LIGHT | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660X5362 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XA5359 | - | HEATER HEAT OFF | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660X5359 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL5363 | - | 660F5001 | LIGHT | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660X5363 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS3-C37-C38 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XA5361 | - | HEATER SHUTDOWN | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660X5361 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL5364 | - | 660F5001 | LIGHT | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660X5364 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS3-C39-C40 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XA5362 | - | FD FAN RUNNING | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 4 | 660X5362 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL5365 | - | 660F5001 | LIGHT | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660X5365 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS3-C41-C42 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL5356 | - | 660F5001 | LIGHT | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660X5356 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS3-C43-C44 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XA5364 | - | ID FAN RUNNING | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660X5364 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL5357 | - | 660F5001 | LIGHT | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660X5357 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS3-C45-C46 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XA5365 | - | ID FAN FAULT | ALARM | - | - | - | N | - | CRD | SdC | SIS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 9 | 660X5365 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XX5378 | - | 660F5001 | HORN | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 11 | 660X5378 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS3-C47-C48 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL5366 | - | 660F5001 | LIGHT | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660X5366 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS3-C49-C50 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL5367 | - | 660F5001 | LIGHT | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | FR-GPS-660-2-TENV-007083 660F5001 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660X5367 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | - | - | - | - | - | - | - | - | - | - | - | 660LP530/TS3-C51-C51 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XE5500 | - | 660K5001 - MACHINE PROTECTION SYSTEM | RADIAL SHALF VIBRATION | - | - | - | - | - | L | - | MAINT | - | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm HH: 90 Alarm H: 60 | - | - | - | 2 | 660X5500 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.25 | mm | - | 2.6 | mm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XE5516 | - | 660K5001 - MACHINE PROTECTION SYSTEM | RADIAL SHALF VIBRATION | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -50 | 50 | ALERT (18g) | g | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660X5516 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | - | - | - | - | - | - | - | - | - | - | - | 660BJIMS535/P01 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660XI5500 | - | 660K5001 - MACHINE PROTECTION SYSTEM | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | to be elaborated by the vendor | to be elaborated by the vendor | to be elaborated by the vendor | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660X5500 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660XAH5500 | - | 660K5001 - MACHINE PROTECTION SYSTEM | ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660X5500 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660XS5500 | 660-XS -5584 | GB LS VIB NDE HH FRO MPS TO S-PLC | CONTACT | - | - | NORMALLY CLOSE | N | - | ITR | ST1D | MAINT | S-PLC | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | FROM ST1C / MMS | - | - | - | 7 | 660X5500 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | N/A | - | By OSBL | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XE5501 | - | 660K5001 - MACHINE PROTECTION SYSTEM | RADIAL SHALF VIBRATION | - | - | - | - | - | L | - | MAINT | - | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm HH: 90 Alarm H: 60 | - | - | - | 2 | 660X5501 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.25 | mm | - | 2.6 | mm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XE5517 | - | 660K5001 - MACHINE PROTECTION SYSTEM | RADIAL SHALF VIBRATION | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -50 | 50 | ALERT (18g) | g | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660X5517 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | - | - | - | - | - | - | - | - | - | - | - | 660BJIMS535/P02 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660XI5501 | - | 660K5001 - MACHINE PROTECTION SYSTEM | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | to be elaborated by the vendor | to be elaborated by the vendor | to be elaborated by the vendor | °C | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660X5501 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660XAH5501 | - | 660K5001 - MACHINE PROTECTION SYSTEM | ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660X5501 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660XL5591 | 660-XL -5501 | OIL PUMP A RUNNING 660LP550 | LIGHT | - | - | - | - | - | LP | ST1D | MAINT | S-PLC | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | FROM ST1 / MMS | - | - | - | 12 | 660X5501 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660LP550/TS2-C09-C10 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XE5502 | - | 660K5001 - MACHINE PROTECTION SYSTEM | RADIAL SHALF VIBRATION | - | - | - | - | - | L | - | MAINT | - | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm HH: 90 Alarm H: 60 | - | - | - | 2 | 660X5502 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.25 | mm | - | 2.6 | mm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XTS5500 | - | 660K5001 - MACHINE PROTECTION SYSTEM | VIBRATION | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0,25 | 2,3 | ALERT (60μm)/ Shutdown (90μm) | mm | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660X5500 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.25 | mm | - | 2.3 | mm | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS535/T03 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660XI5502 | - | 660K5001 - MACHINE PROTECTION SYSTEM | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660X5502 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660XAH5502 | - | 660K5001 - MACHINE PROTECTION SYSTEM | ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660X5502 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660XS5502 | 660-XS -5583 | GB LS VIB DE HH FROM MPS TO S-PLC | CONTACT | - | - | NORMALLY CLOSE | N | - | ITR | ST1D | MAINT | S-PLC | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | FROM ST1C / MMS | - | - | - | 7 | 660X5502 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | N/A | - | By OSBL | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XE5503 | - | 660K5001 - MACHINE PROTECTION SYSTEM | RADIAL SHALF VIBRATION | - | - | - | - | - | L | - | MAINT | - | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm HH: 90 Alarm H: 60 | - | - | - | 2 | 660X5503 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.25 | mm | - | 2.6 | mm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XTS5501 | - | 660K5001 - MACHINE PROTECTION SYSTEM | VIBRATION | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0,25 | 2,3 | ALERT (60μm)/ Shutdown (90μm) | mm | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660X5501 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.25 | mm | - | 2.3 | mm | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS535/T04 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660XI5503 | - | 660K5001 - MACHINE PROTECTION SYSTEM | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660X5503 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660XAH5503 | - | 660K5001 - MACHINE PROTECTION SYSTEM | ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660X5503 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XE5504 | - | 660K5001 - MACHINE PROTECTION SYSTEM | RADIAL SHALF VIBRATION | - | - | - | - | - | L | - | MAINT | - | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm HH: 59 Alarm H: 39 | - | - | - | 2 | 660X5504 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.25 | mm | - | 2.6 | mm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XTS5502 | - | 660K5001 - MACHINE PROTECTION SYSTEM | VIBRATION | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0,25 | 2,3 | ALERT (60μm)/ Shutdown (90μm) | mm | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660X5502 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.25 | mm | - | 2.3 | mm | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS535/T05 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660XI5504 | - | 660K5001 - MACHINE PROTECTION SYSTEM | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660X5504 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660XAH5504 | - | 660K5001 - MACHINE PROTECTION SYSTEM | ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660X5504 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660XS5504 | 660-XS -5585 | GB HS VIB DE HH FROM MPS TO S-PLC | CONTACT | - | - | NORMALLY CLOSE | N | - | ITR | ST1D | MAINT | S-PLC | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | FROM ST1C / MMS | - | - | - | 7 | 660X5504 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | N/A | - | By OSBL | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XE5505 | - | 660K5001 - MACHINE PROTECTION SYSTEM | RADIAL SHALF VIBRATION | - | - | - | - | - | L | - | MAINT | - | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm HH: 59 Alarm H: 39 | - | - | - | 2 | 660X5505 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.25 | mm | - | 2.6 | mm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XTS5503 | - | 660K5001 - MACHINE PROTECTION SYSTEM | VIBRATION | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0,25 | 2,3 | ALERT (60μm)/ Shutdown (90μm) | mm | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660X5503 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.25 | mm | - | 2.3 | mm | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS535/T06 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660XI5505 | - | 660K5001 - MACHINE PROTECTION SYSTEM | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660X5505 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660XAH5505 | - | 660K5001 - MACHINE PROTECTION SYSTEM | ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660X5505 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XE5506 | - | 660K5001 - MACHINE PROTECTION SYSTEM | RADIAL SHALF VIBRATION | - | - | - | - | - | L | - | MAINT | - | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm HH: 59 Alarm H: 39 | - | - | - | 2 | 660X5506 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.25 | mm | - | 2.6 | mm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XTS5504 | - | 660K5001 - MACHINE PROTECTION SYSTEM | VIBRATION | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0,25 | 2,3 | ALERT (60μm)/ Shutdown (90μm) | mm | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660X5504 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.25 | mm | - | 2.3 | mm | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS535/T07 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660XI5506 | - | 660K5001 - MACHINE PROTECTION SYSTEM | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660X5506 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660XAH5506 | - | 660K5001 - MACHINE PROTECTION SYSTEM | ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660X5506 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660XS5506 | 660-XS -5586 | GB HS VIB NDE HH FROM MPS TO S-PLC | CONTACT | - | - | NORMALLY CLOSE | N | - | ITR | ST1D | MAINT | S-PLC | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | FROM ST1C / MMS | - | - | - | 7 | 660X5506 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | N/A | - | By OSBL | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XE5507 | - | 660K5001 - MACHINE PROTECTION SYSTEM | RADIAL SHALF VIBRATION | - | - | - | - | - | L | - | MAINT | - | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm HH: 59 Alarm H: 39 | - | - | - | 2 | 660X5507 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.25 | mm | - | 2.6 | mm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XTS5505 | - | 660K5001 - MACHINE PROTECTION SYSTEM | VIBRATION | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0,25 | 2,3 | ALERT (60μm)/ Shutdown (90μm) | mm | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660X5505 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.25 | mm | - | 2.3 | mm | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS535/T08 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660XI5507 | - | 660K5001 - MACHINE PROTECTION SYSTEM | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660X5507 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660XAH5507 | - | 660K5001 - MACHINE PROTECTION SYSTEM | ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660X5507 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XE5508 | - | 660K5001 - MACHINE PROTECTION SYSTEM | RADIAL SHALF VIBRATION | - | - | - | - | - | L | - | MAINT | - | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm HH: 61.8 Alarm H: 71.3 | - | - | - | 2 | 660X5508 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | µm | - | 150 | µm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660ZT5006 | 660-ZT -5506 | 660K5001 - MACHINE PROTECTION SYSTEM | AXIAL DISPLACEMEN | - | - | - | N | - | L | ST1C | MAINT | MMS | - | to be elaborated by the client | to be elaborated by the client | to be elaborated by the client | mm | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660Z5006 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | - | - | - | - | - | - | - | - | - | - | - | 660BJIMS560/TS2-P01 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660XI5508 | - | 660K5001 - MACHINE PROTECTION SYSTEM | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660X5508 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660XAH5508 | - | 660K5001 - MACHINE PROTECTION SYSTEM | ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660X5508 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660XS5508 | - | COMP VIB SHAFT MD | CONTACT | - | - | NORMALLY CLOSE | N | - | ITR | ST1D | MAINT | S-PLC | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | FROM ST1C / MMS | - | - | - | 7 | 660X5508 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | N/A | - | By OSBL | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XE5509 | - | 660K5001 - MACHINE PROTECTION SYSTEM | RADIAL SHALF VIBRATION | - | - | - | - | - | L | - | MAINT | - | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm HH: 61.8 Alarm H: 71.3 | - | - | - | 2 | 660X5509 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | µm | - | 150 | µm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660ZT5007 | - | 660K5001 - MACHINE PROTECTION SYSTEM | AXIAL DISPLACEMEN | - | - | - | N | - | L | ST1C | MAINT | MMS | - | to be elaborated by the client | to be elaborated by the client | to be elaborated by the client | mm | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660Z5007 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | - | - | - | - | - | - | - | - | - | - | - | 660BJIMS525/P13 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660XI5509 | - | 660K5001 - MACHINE PROTECTION SYSTEM | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660X5509 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660XAH5509 | - | 660K5001 - MACHINE PROTECTION SYSTEM | ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660X5509 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XE5510 | - | 660K5001 - MACHINE PROTECTION SYSTEM | RADIAL SHALF VIBRATION | - | - | - | - | - | L | - | MAINT | - | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm HH: 61.8 Alarm H: 71.3 | - | - | - | 2 | 660X5510 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | µm | - | 150 | µm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660ZT5500A | - | 660K5001 - MACHINE PROTECTION SYSTEM | AXIAL DISPLACEMEN | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0,25 | 2,3 | ALERT (0,35mm) / Shutdown (0,4mm) | mm | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660Z5500 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.25 | mm | - | 2.3 | mm | - | - | - | - | - | - | AI20 | - | - | - | - | - | - | - | - | - | - | - | 660BJIMS535/T11 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660XI5510 | - | 660K5001 - MACHINE PROTECTION SYSTEM | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660X5510 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660XAH5510 | - | 660K5001 - MACHINE PROTECTION SYSTEM | ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660X5510 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660XS5510 | - | COMP VIB SHAFT FD | CONTACT | - | - | NORMALLY CLOSE | N | - | ITR | ST1D | MAINT | S-PLC | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | FROM ST1C / MMS | - | - | - | 7 | 660X5510 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | N/A | - | By OSBL | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XE5511 | - | 660K5001 - MACHINE PROTECTION SYSTEM | RADIAL SHALF VIBRATION | - | - | - | - | - | L | - | MAINT | - | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm HH: 61.8 Alarm H: 71.3 | - | - | - | 2 | 660X5511 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | µm | - | 150 | µm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660ZT5500B | - | 660K5001 - MACHINE PROTECTION SYSTEM | AXIAL DISPLACEMEN | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0,25 | 2,3 | ALERT (0,35mm) / Shutdown (0,4mm) | mm | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660Z5500 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.25 | mm | - | 2.3 | mm | - | - | - | - | - | - | AI20 | - | - | - | - | - | - | - | - | - | - | - | 660BJIMS535/T12 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660XI5511 | - | 660K5001 - MACHINE PROTECTION SYSTEM | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660X5511 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660XAH5511 | - | 660K5001 - MACHINE PROTECTION SYSTEM | ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660X5511 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XE5512 | - | 660K5001 - MACHINE PROTECTION SYSTEM | RADIAL SHALF VIBRATION | - | - | - | - | - | L | - | MAINT | - | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm HH: 61.8 Alarm H: 71.3 | - | - | - | 2 | 660X5512 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | µm | - | 150 | µm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XTS5508 | - | 660K5001 - MACHINE PROTECTION SYSTEM | VIBRATION | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0,25 | 2,3 | ALERT (60μm)/ Shutdown (90μm) | mm | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660X5508 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | µm | - | 150 | µm | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS525/P05 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660XI5512 | - | 660K5001 - MACHINE PROTECTION SYSTEM | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660X5512 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660XAH5512 | - | 660K5001 - MACHINE PROTECTION SYSTEM | ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660X5512 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660XS5512 | - | COMP VIB SHAFT MS | CONTACT | - | - | NORMALLY CLOSE | N | - | ITR | ST1D | MAINT | S-PLC | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | FROM ST1C / MMS | - | - | - | 7 | 660X5512 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | N/A | - | By OSBL | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XE5513 | - | 660K5001 - MACHINE PROTECTION SYSTEM | RADIAL SHALF VIBRATION | - | - | - | - | - | L | - | MAINT | - | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm HH: 61.8 Alarm H: 71.3 | - | - | - | 2 | 660X5513 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | µm | - | 150 | µm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XTS5509 | - | 660K5001 - MACHINE PROTECTION SYSTEM | VIBRATION | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 150 | ALERT (61,8μm) / Shutdown (71,3μm) | μm | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660X5509 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | µm | - | 150 | µm | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS525/P06 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660XI5513 | - | 660K5001 - MACHINE PROTECTION SYSTEM | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660X5513 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660XAH5513 | - | 660K5001 - MACHINE PROTECTION SYSTEM | ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660X5513 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XE5514 | - | 660K5001 - MACHINE PROTECTION SYSTEM | RADIAL SHALF VIBRATION | - | - | - | - | - | L | - | MAINT | - | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm HH: 61.8 Alarm H: 71.3 | - | - | - | 2 | 660X5514 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | µm | - | 150 | µm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XTS5510 | - | 660K5001 - MACHINE PROTECTION SYSTEM | VIBRATION | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 150 | ALERT (61,8μm) / Shutdown (71,3μm) | μm | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660X5510 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | µm | - | 150 | µm | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS525/P07 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660XI5514 | - | 660K5001 - MACHINE PROTECTION SYSTEM | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660X5514 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660XAH5514 | - | 660K5001 - MACHINE PROTECTION SYSTEM | ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660X5514 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660XS5514 | - | COMP VIB SHAFT FS | CONTACT | - | - | NORMALLY CLOSE | N | - | ITR | ST1D | MAINT | S-PLC | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | FROM ST1C / MMS | - | - | - | 7 | 660X5514 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | N/A | - | By OSBL | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XE5515 | - | 660K5001 - MACHINE PROTECTION SYSTEM | RADIAL SHALF VIBRATION | - | - | - | - | - | L | - | MAINT | - | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm HH: 61.8 Alarm H: 71.3 | - | - | - | 2 | 660X5515 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | µm | - | 150 | µm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XTS5511 | - | 660K5001 - MACHINE PROTECTION SYSTEM | VIBRATION | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 150 | ALERT (61,8μm) / Shutdown (71,3μm) | μm | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660X5511 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | µm | - | 150 | µm | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS525/P08 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660XI5515 | - | 660K5001 - MACHINE PROTECTION SYSTEM | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660X5515 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660XAH5515 | - | 660K5001 - MACHINE PROTECTION SYSTEM | ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660X5515 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XTS5506 | - | 660K5001 - MACHINE PROTECTION SYSTEM | VIBRATION | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0,25 | 2,3 | ALERT (60μm)/ Shutdown (90μm) | mm | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660X5506 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.25 | mm | - | 2.3 | mm | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS535/T09 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XI5516 | - | HOLD | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660X5516 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660XAH5516 | - | HOLD | ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660X5516 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660XT5516 | - | Casing vibration Gear box 660-KRB-5001 | ACCELEROMETER | - | - | - | - | - | L | ST1C | MAINT | MMS | - | -50 | 50 | ALERT (18g) | g | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 18 | - | - | - | 3 | 660X5516 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -50 | g | - | 50 | g | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XTS5507 | - | 660K5001 - MACHINE PROTECTION SYSTEM | VIBRATION | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0,25 | 2,3 | ALERT (60μm)/ Shutdown (90μm) | mm | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660X5507 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.25 | mm | - | 2.3 | mm | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS535/T10 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XI5517 | - | HOLD | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660X5517 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660XAH5517 | - | HOLD | ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660X5517 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660XT5517 | - | Casing vibration Gear box 660-KRB-5001 | ACCELEROMETER | - | - | - | - | - | L | ST1C | MAINT | MMS | - | -50 | 50 | ALERT (18g) | g | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm H: 18 | - | - | - | 3 | 660X5517 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -50 | g | - | 50 | g | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XS5518 | - | HAND SWITCH IN COMPRESSOR | CONTACT | - | - | NORMALLY CLOSE | N | - | ITR | ST1D | MAINT | S-PLC | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | FROM ST1C / MMS | - | - | - | 7 | 660X5518 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | By OSBL | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XI5518 | - | 660 K 5001 VIBRATION COMPRESSOR | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660X5518 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XE5518 | - | 660 K 5001 VIBRATION COMPRESSOR | RADIAL SHALF VIBRATION | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -50 | 50 | ALERT (20 m/s²) / Shutdown (30 m/s²) | g | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660X5518 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660BJIMS560/TS1-P01 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660XAH5518 | - | 660 K 5001 VIBRATION COMPRESSOR | ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660X5518 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660XTS5518 | - | 660G5001A-RADIAL VIBRATION SENSOR (ACCELEROMETER) | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -50 | 50 | ALERT (20 m/s²) / Shutdown (30 m/s²) | g | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | GEARBOX OR PUMP Alarm HH: 30 Alarm H: 20 | - | - | - | 3 | 660X5518 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -50 | g | - | 50 | g | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS531/P01 | - | E10101 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XE5519 | - | 660 K 5001 VIBRATION COMPRESSOR | RADIAL SHALF VIBRATION | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -50 | 50 | ALERT (20 m/s²) / Shutdown (30 m/s²) | g | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660X5519 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660BJIMS560/TS1-P02 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XI5519 | - | 660 K 5001 VIBRATION COMPRESSOR | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660X5519 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660XAH5519 | - | 660 K 5001 VIBRATION COMPRESSOR | ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660X5519 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660XTS5519 | - | 660G5001A-RADIAL VIBRATION SENSOR (ACCELEROMETER) | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -50 | 50 | ALERT (20 m/s²) / Shutdown (30 m/s²) | g | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | GEARBOX OR PUMP Alarm HH: 30 Alarm H: 20 | - | - | - | 3 | 660X5519 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -50 | g | - | 50 | g | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS531/P02 | - | E10101 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XE5520 | - | 660 K 5001 VIBRATION COMPRESSOR | RADIAL SHALF VIBRATION | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -50 | 50 | ALERT (20 m/s²) / Shutdown (30 m/s²) | g | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660X5520 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660BJIMS560/TS1-P03 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XI5520 | - | 660 K 5001 VIBRATION COMPRESSOR | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660X5520 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660XAH5520 | - | 660 K 5001 VIBRATION COMPRESSOR | ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660X5520 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660XTS5520 | - | 660G5001A-RADIAL VIBRATION SENSOR (ACCELEROMETER) | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -50 | 50 | ALERT (20 m/s²) / Shutdown (30 m/s²) | g | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | GEARBOX OR PUMP Alarm HH: 30 Alarm H: 20 | - | - | - | 3 | 660X5520 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -50 | g | - | 50 | g | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS531/P03 | - | E10101 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660XS5520 | 660-XS -5587 | 660K5001 MOTOR VIB HH FROM MPS TO S-PLC | CONTACT | - | - | NORMALLY CLOSE | N | - | ITR | ST1D | MAINT | S-PLC | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | FROM ST1C / MMS | - | - | - | 7 | 660X5520 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | N/A | - | By OSBL | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XE5521 | - | 660 K 5001 VIBRATION COMPRESSOR | RADIAL SHALF VIBRATION | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -50 | 50 | ALERT (20 m/s²) / Shutdown (30 m/s²) | g | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 2 | 660X5521 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660BJIMS560/TS1-P04 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XI5521 | - | 660 K 5001 VIBRATION COMPRESSOR | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660X5521 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660XAH5521 | - | 660 K 5001 VIBRATION COMPRESSOR | ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660X5521 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660XTS5521 | - | 660G5001A-RADIAL VIBRATION SENSOR (ACCELEROMETER) | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -50 | 50 | ALERT (20 m/s²) / Shutdown (30 m/s²) | g | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | GEARBOX OR PUMP Alarm HH: 30 Alarm H: 20 | - | - | - | 3 | 660X5521 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -50 | g | - | 50 | g | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS531/P04 | - | E10101 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XTS5522 | - | 660G5001A-MOTOR BEARING RADIAL VIBRATION SENSOR (ACC | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 1270 | Alarm High(6.2) / Alarm High High (10) | mm/s RMS | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | MOTOR | - | - | - | 3 | 660X5522 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS531/P05 | - | E10101 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XX5522 | - | 660 K 5001 VIBRATION COMPRESSOR | HORN | - | - | - | - | - | L | - | MAINT | S-PLC | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 1 | 660X5522 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | - | - | - | - | - | - | - | - | - | - | - | 660BJCS510/C01-C02 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660XA5522 | - | 660 K 5001 VIBRATION COMPRESSOR | ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660X5522 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XTS5523 | - | 660G5001A-MOTOR BEARING RADIAL VIBRATION SENSOR (ACC | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 1270 | Alarm High(6.2) / Alarm High High (10) | mm/s RMS | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | MOTOR | - | - | - | 3 | 660X5523 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS531/P06 | - | E10101 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XL5523 | - | 660 K 5001 VIBRATION COMPRESSOR | LIGHT | - | - | - | - | - | L | - | MAINT | S-PLC | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 12 | 660X5523 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | - | - | - | - | - | - | - | - | - | - | - | 660BJCS510/C03-C04 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660XA5523 | - | 660 K 5001 VIBRATION COMPRESSOR | ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660X5523 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XTS5524 | - | 660G5001A-MOTOR BEARING RADIAL VIBRATION SENSOR (ACC | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 1270 | Alarm High(6.2) / Alarm High High (10) | mm/s RMS | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | MOTOR | - | - | - | 3 | 660X5524 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS531/P07 | - | E10101 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XTS5525 | - | 660G5001A-MOTOR BEARING RADIAL VIBRATION SENSOR (ACC | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 1270 | Alarm High(6.2) / Alarm High High (10) | mm/s RMS | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | MOTOR | - | - | - | 3 | 660X5525 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS531/P08 | - | E10101 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XTS5526 | - | 660G5001B-RADIAL VIBRATION SENSOR (ACCELEROMETER) | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 1270 | Alarm High(6.2) / Alarm High High (10) | mm/s RMS | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | GEARBOX OR PUMP | - | - | - | 3 | 660X5526 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS532/P01 | - | E10101 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XTS5527 | - | 660G5001B-RADIAL VIBRATION SENSOR (ACCELEROMETER) | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 1270 | Alarm High(6.2) / Alarm High High (10) | mm/s RMS | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | GEARBOX OR PUMP | - | - | - | 3 | 660X5527 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS532/P02 | - | E10101 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XTS5528 | - | 660G5001B-RADIAL VIBRATION SENSOR (ACCELEROMETER) | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 1270 | Alarm High(6.2) / Alarm High High (10) | mm/s RMS | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | GEARBOX OR PUMP | - | - | - | 3 | 660X5528 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS532/P03 | - | E10101 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XTS5529 | - | 660G5001B-RADIAL VIBRATION SENSOR (ACCELEROMETER) | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 1270 | Alarm High(6.2) / Alarm High High (10) | mm/s RMS | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | GEARBOX OR PUMP | - | - | - | 3 | 660X5529 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS532/P04 | - | E10101 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XTS5530 | - | 660G5001B-MOTOR BEARING RADIAL VIBRATION SENSOR (ACC | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 1270 | Alarm High(6.2) / Alarm High High (10) | mm/s RMS | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | MOTOR | - | - | - | 3 | 660X5530 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS532/P05 | - | E10101 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XL5530 | - | AUXILIARY STANBY 660LP550 | LIGHT | - | - | - | N | - | LP | ST1D | MAINT | S-PLC | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | FROM ST1 / MMS | - | - | - | 12 | 660X5530 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660LP550/TS2-C01-C02 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XTS5531 | - | 660G5001B-MOTOR BEARING RADIAL VIBRATION SENSOR (ACC | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 1270 | Alarm High(6.2) / Alarm High High (10) | mm/s RMS | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | MOTOR | - | - | - | 3 | 660X5531 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS532/P06 | - | E10101 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XL5531 | - | 660K5001 TRIP FROM MPS TO S-PLC | LIGHT | - | - | - | N | - | LP | ST1D | MAINT | S-PLC | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | FROM ST1 / MMS | - | - | - | 12 | 660X5531 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660LP550/TS2-C03-C04 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660XS5531 | 660-XS -5581 | 660K5001 COMMON ALERT FROM MPS TO S-PLC | CONTACT | - | - | NORMALLY CLOSE | N | - | ITR | ST1D | MAINT | S-PLC | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | FROM ST1C / MMS | - | - | - | 7 | 660X5531 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | N/A | - | By OSBL | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XTS5532 | - | 660G5001B-MOTOR BEARING RADIAL VIBRATION SENSOR (ACC | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 1270 | Alarm High(6.2) / Alarm High High (10) | mm/s RMS | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | MOTOR | - | - | - | 3 | 660X5532 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS532/P07 | - | E10101 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XS5532 | 660-XS -5582 | 660K5001 COMMON UNSAFE FROM MPS TO S-PLC | CONTACT | - | - | NORMALLY CLOSE | N | - | ITR | ST1D | MAINT | S-PLC | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | FROM ST1C / MMS | - | - | - | 7 | 660X5532 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | N/A | - | By OSBL | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XTS5533 | - | 660G5001B-MOTOR BEARING RADIAL VIBRATION SENSOR (ACC | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 1270 | Alarm High(6.2) / Alarm High High (10) | mm/s RMS | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | MOTOR | - | - | - | 3 | 660X5533 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS532/P08 | - | E10101 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XL5533 | - | START UP/ SHUT DOWN PROCEDURE 660LP550 | LIGHT | - | - | - | - | - | LP | ST1D | MAINT | S-PLC | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | FROM ST1 / MMS | - | - | - | 12 | 660X5533 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660LP550/TS2-C05-C06 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660XS5533 | 660-XS -5580 | 660K5001 RESET SHUTDOWN FROM MPS TO S-PLC | CONTACT | - | - | NORMALLY CLOSE | N | - | ITR | ST1D | MAINT | S-PLC | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | FROM ST1C / MMS | - | - | - | 7 | 660X5533 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | N/A | - | By OSBL | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XTS5534 | - | 660G5002A-RADIAL VIBRATION SENSOR (ACCELEROMETER) | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 1270 | Alarm High (6.2) / HighHigh(10) | mm/s RMS | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | GEARBOX OR PUMP | - | - | - | 3 | 660X5534 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS530/P01 | - | E10101 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XTS5535 | - | 660G5002B-RADIAL VIBRATION SENSOR (ACCELEROMETER) | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 1270 | Alarm High (6.2) / HighHigh(10) | mm/s RMS | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | GEARBOX OR PUMP | - | - | - | 3 | 660X5535 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS536/P01 | - | E10101 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XL5535 | - | COMMON ALARM 660LP550 | LIGHT | - | - | - | N | - | LP | ST1D | MAINT | S-PLC | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | FROM ST1 / MMS | - | - | - | 12 | 660X5535 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660LP550/TS2-C07-C08 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XTS5536 | - | 660G5003A-RADIAL VIBRATION SENSOR (ACCELEROMETER) | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 1270 | Alarm High(6.2) / Alarm High High (10) | mm/s RMS | FR-GPS-100-0-FLOW-002121 | - | - | - | - | 660-2-Fractionation | GEARBOX OR PUMP | - | - | - | 3 | 660X5536 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS530/P02 | - | E10101 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XTS5537 | - | 660G5003B-RADIAL VIBRATION SENSOR (ACCELEROMETER) | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 1270 | Alarm High(6.2) / Alarm High High (10) | mm/s RMS | FR-GPS-100-0-FLOW-002121 | - | - | - | - | 660-2-Fractionation | GEARBOX OR PUMP | - | - | - | 3 | 660X5537 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS536/P02 | - | E10101 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XTS5540 | - | 660G5001B-RADIAL VIBRATION SENSOR (ACCELEROMETER) | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 1270 | Alarm High(6.2) / Alarm High High (10) | mm/s RMS | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | MOTOR | - | - | - | 3 | 660X5540 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS532/P09 | - | E10101 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XTS5541 | - | 660G5001B-RADIAL VIBRATION SENSOR (ACCELEROMETER) | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 1270 | Alarm High(6.2) / Alarm High High (10) | mm/s RMS | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | MOTOR | - | - | - | 3 | 660X5541 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS532/P10 | - | E10101 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XTS5542 | - | 660G5001A-MOTOR BEARING RADIAL VIBRATION SENSOR (ACC | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 1270 | Alarm High(6.2) / Alarm High High (10) | mm/s RMS | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | MOTOR | - | - | - | 3 | 660X5542 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS531/P09 | - | E10101 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XTS5543 | - | 660G5001A-MOTOR BEARING RADIAL VIBRATION SENSOR (ACC | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 1270 | Alarm High(6.2) / Alarm High High (10) | mm/s RMS | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | MOTOR | - | - | - | 3 | 660X5543 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS531/P10 | - | E10101 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XS5550 | - | 660G5001A TRIP FROM MPS TO S-PLC | CONTACT | - | - | NORMALLY CLOSE | N | - | ITR | ST1D | MAINT | S-PLC | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | FROM ST1C / MMS | - | - | - | 7 | 660X5550 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | N/A | - | By OSBL | - | - | - | - | - | 24 VDC-MMS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XS5551 | - | 660G5001A TRIP FROM MPS TO S-PLC | CONTACT | - | - | NORMALLY CLOSE | N | - | ITR | ST1D | MAINT | S-PLC | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | FROM ST1C / MMS | - | - | - | 7 | 660X5551 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | N/A | - | By OSBL | - | - | - | - | - | 24 VDC-MMS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XS5552 | - | 660G5001A TRIP FROM MPS TO S-PLC | CONTACT | - | - | NORMALLY CLOSE | N | - | ITR | ST1D | MAINT | S-PLC | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | FROM ST1C / MMS | - | - | - | 7 | 660X5552 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | N/A | - | By OSBL | - | - | - | - | - | 24 VDC-MMS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XS5553 | - | 660G5001A TRIP FROM MPS TO S-PLC | CONTACT | - | - | NORMALLY CLOSE | N | - | ITR | ST1D | MAINT | S-PLC | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | FROM ST1C / MMS | - | - | - | 7 | 660X5553 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | N/A | - | By OSBL | - | - | - | - | - | 24 VDC-MMS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XS5555 | - | 660G5001B TRIP FROM MPS TO S-PLC | CONTACT | - | - | NORMALLY CLOSE | N | - | ITR | ST1D | MAINT | S-PLC | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | FROM ST1C / MMS | - | - | - | 7 | 660X5555 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | N/A | - | By OSBL | - | - | - | - | - | 24 VDC-MMS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XS5556 | - | 660G5001B TRIP FROM MPS TO S-PLC | CONTACT | - | - | NORMALLY CLOSE | N | - | ITR | ST1D | MAINT | S-PLC | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | FROM ST1C / MMS | - | - | - | 7 | 660X5556 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | N/A | - | By OSBL | - | - | - | - | - | 24 VDC-MMS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XS5557 | - | 660G5001B TRIP FROM MPS TO S-PLC | CONTACT | - | - | NORMALLY CLOSE | N | - | ITR | ST1D | MAINT | S-PLC | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | FROM ST1C / MMS | - | - | - | 7 | 660X5557 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | N/A | - | By OSBL | - | - | - | - | - | 24 VDC-MMS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XS5558 | - | 660G5001B TRIP FROM MPS TO S-PLC | CONTACT | - | - | NORMALLY CLOSE | N | - | ITR | ST1D | MAINT | S-PLC | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | FROM ST1C / MMS | - | - | - | 7 | 660X5558 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | N/A | - | By OSBL | - | - | - | - | - | 24 VDC-MMS | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XS5560 | - | 660G5002A TRIP FROM MPS TO S-PLC | CONTACT | - | - | NORMALLY CLOSE | - | - | ITR | ST1D | MAINT | S-PLC | - | - | - | - | - | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | FROM ST1C / MMS | - | - | - | 7 | 660X5560 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | N/A | - | By OSBL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XS5561 | - | 660G5002B TRIP FROM MPS TO S-PLC | CONTACT | - | - | NORMALLY CLOSE | - | - | ITR | ST1D | MAINT | S-PLC | - | - | - | - | - | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | FROM ST1C / MMS | - | - | - | 7 | 660X5561 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | N/A | - | By OSBL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XS5562 | - | 660G5003A TRIP FROM MPS TO S-PLC | CONTACT | - | - | NORMALLY CLOSE | - | - | ITR | ST1D | MAINT | S-PLC | - | - | - | - | - | FR-GPS-100-0-FLOW-002121 | - | - | - | - | 660-2-Fractionation | FROM ST1C / MMS | - | - | - | 7 | 660X5562 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | N/A | - | By OSBL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XS5563 | - | 660G5003B TRIP FROM MPS TO S-PLC | CONTACT | - | - | NORMALLY CLOSE | - | - | ITR | ST1D | MAINT | S-PLC | - | - | - | - | - | FR-GPS-100-0-FLOW-002121 | - | - | - | - | 660-2-Fractionation | FROM ST1C / MMS | - | - | - | 7 | 660X5563 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | N/A | - | By OSBL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XS5570 | - | INTERCONECTION SIGNAL TO MCC - SIS STOP HEATER | CONTACT | - | - | NORMALLY CLOSE | N | - | ITR | ST1D | MAINT | S-PLC | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | FROM ST1C / MMS | - | - | - | 7 | 660X5570 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | N/A | - | By OSBL | - | - | - | - | - | 24 VDC-MMS | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XS5571 | - | INTERCONECTION MCC-SIS START HEATER | CONTACT | - | - | NORMALLY CLOSE | N | - | ITR | ST1D | MAINT | S-PLC | - | - | - | - | - | P22201-100-02 | - | - | - | - | 660-2-Fractionation | FROM ST1C / MMS | - | - | - | 7 | 660X5571 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | N/A | - | By OSBL | - | - | - | - | - | 24 VDC-MMS | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC11 | - | 1 | - | 1 | - | 660XS_5575_A | - | 660K5004 ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | N | - | ITR | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 100 -Fire and Gas | DO Corresponding to S-PLC DI (660XS5575A) | - | - | - | 7 | 660X5575 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC11 | - | 1 | - | 1 | - | 660XS_5575_B | - | 660K5004 ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | N | - | ITR | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 100 -Fire and Gas | DO Corresponding to S-PLC DI (660XS5575B) | - | - | - | 7 | 660X5575 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC11 | - | 1 | - | 1 | - | 660XS_5575_C | - | 660K5004 ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | N | - | ITR | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 100 -Fire and Gas | DO Corresponding to S-PLC DI (660XS5575C) | - | - | - | 7 | 660X5575 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC11 | - | 0 | - | 1 | - | 660XS5575A | - | 660K5004 ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | N | - | ITR | ST1C | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660X5575 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC11 | - | 1 | - | 1 | - | 660XS5575B | - | 660K5004 ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | N | - | ITR | ST1C | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660X5575 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC11 | - | 2 | - | 1 | - | 660XS5575C | - | 660K5004 ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | N | - | ITR | ST1C | SIS | S-PLC | - | - | - | - | - | 214359C-6602-PID-0021-0212 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660X5575 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL5592 | - | 660K5001 - MACHINE PROTECTION SYSTEM | LIGHT | - | - | - | N | - | LP | ST1D | SIS | S-PLC | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | FROM ST1 / MMS | - | - | - | 12 | 660X5592 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | 660LP550/TS2-C11-C12 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL_5901 | - | 660-2 BEACON ALARM(GAS & FIRE) | FLASHING LIGHT | - | - | - | N | - | L | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 7 | 660XL5901 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJCS506/C01-C02 | - | E11206 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL_5902 | - | 660-2 BEACON ALARM(GAS) | FLASHING LIGHT | - | - | - | N | - | L | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 7 | 660XL5902 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJCS506/C03-C04 | - | E11206 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL_5903 | - | 660-2 BEACON ALARM(GAS) | FLASHING LIGHT | - | - | - | N | - | L | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 7 | 660XL5903 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJCS506/C05-C06 | - | E11206 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL_5904 | - | 660-2 BEACON ALARM(GAS & FIRE) | FLASHING LIGHT | - | - | - | N | - | L | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 7 | 660XL5904 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJCS506/C07-C08 | - | E11206 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL_5981 | - | 660-2 BEACON ALARM(FLAMMABLE F) | FLASHING LIGHT | - | - | - | N | - | AS | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 7 | 660XL5981 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJCS591/C05-C06 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL_5982 | - | 660-2 BEACON ALARM(GAS) | FLASHING LIGHT | - | - | - | - | - | AS | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 7 | 660XL5982 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL_5983 | - | 660-2 BEACON ALARM(OXIGEN DEFICIENCY) | FLASHING LIGHT | - | - | - | - | - | AS | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 7 | 660XL5983 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL_5984 | - | 660-2 BEACON ALARM(FLAMMABLE F) | FLASHING LIGHT | - | - | - | - | - | AS | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 7 | 660XL5984 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJCS591/C07-C08 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL_5985 | - | 660-2 BEACON ALARM(GAS) | FLASHING LIGHT | - | - | - | N | - | AS | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 7 | 660XL5985 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XL_5986 | - | 660-2 BEACON ALARM(OXIGEN DEFICIENCY) | FLASHING LIGHT | - | - | - | N | - | AS | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 7 | 660XL5986 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XS_5988 | - | FIRE ALARM TO LA35 HVAC | CONTACT | - | - | NORMALLY CLOSE | N | - | AS | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 7 | 660XS5988 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XS_5989 | - | LA35 HVAC STATUS | CONTACT | - | - | NORMALLY CLOSE | N | - | AS | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 7 | 660XS5989 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XX_5901 | - | 660-2 AUDIBLE ALARM | SIREN | - | - | - | N | - | L | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 7 | 660XX5901 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DOS10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJCS506/C09-C10 | - | E11206 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XX_5902 | - | 660-2 AUDIBLE ALARM | SIREN | - | - | - | N | - | L | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 7 | 660XX5902 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DOS10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJCS506/C11-C12 | - | E11206 | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T6 | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XX_5981 | - | 660-2 AUDIBLE ALARM | SIREN | - | - | - | - | - | AS | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 7 | 660XX5981 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DOS10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XX_5982 | - | 660-2 AUDIBLE ALARM | SIREN | - | - | - | N | - | AS | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 7 | 660XX5982 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DOS10 | INT | - | - | - | - | - | - | - | - | - | - | 660BJCS591/C01-C02 | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660XX_5987 | - | 660-2 AUDIBLE ALARM | SIREN | - | - | - | - | - | AS | ST1B | SIS | S-PLC-FGS | - | - | - | - | - | 214359C-1000-DW-1950-0001 | - | - | - | - | 100 -Fire and Gas | - | - | - | - | 7 | 660XX5987 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DOS10 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660ZTS0509 | - | 660G0002-SHAFT AXIAL DISPLACEMENT (ACCELEROMETER) | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | to be elaborated by the client | to be elaborated by the client | to be elaborated by the client | - | FR-GPS-660-2-TENV-660G0002 MMS | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660Z0509 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY MECHANICAL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJIMS533/P03 | - | E10101 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660ZTS0510 | - | 660G0102-SHAFT AXIAL DISPLACEMENT (ACCELEROMETER) | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | to be elaborated by the client | to be elaborated by the client | to be elaborated by the client | - | FR-GPS-660-2-TENV-660G0102 MMS | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660Z0510 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY MECHANICAL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJIMS534/P03 | - | E10101 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660ZTS0511 | - | 660G0003-SHAFT AXIAL DISPLACEMENT (ACCELEROMETER) | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | to be elaborated by the client | to be elaborated by the client | to be elaborated by the client | - | FR-GPS-660-2-TENV-660G0003 MMS | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660Z0511 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY MECHANICAL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJIMS533/P04 | - | E10101 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660ZTS0512 | - | 660G0103-SHAFT AXIAL DISPLACEMENT (ACCELEROMETER) | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | to be elaborated by the client | to be elaborated by the client | to be elaborated by the client | - | FR-GPS-660-2-TENV-660G0103 MMS | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660Z0512 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | BY MECHANICAL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | NR | - | - | - | - | - | - | - | - | - | 660BJIMS534/P04 | - | E10101 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660ZT5501A | - | 660K5001 - MACHINE PROTECTION SYSTEM | AXIAL DISPLACEMEN | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -1 | 1 | ALERT (0,3mm) / Shutdown (0,4mm) | mm | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660Z5501 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -1 | mm | - | 1 | mm | - | - | - | - | - | - | AI20 | - | - | - | - | - | - | - | - | - | - | - | 660BJIMS525/P01 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XTS5512 | - | 660K5001 - MACHINE PROTECTION SYSTEM | VIBRATION | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 150 | ALERT (61,8μm) / Shutdown (71,3μm) | μm | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660X5512 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | µm | - | 150 | µm | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS525/P09 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660FL5390 | - | HOLD | FLOW SWTICH | - | - | - | - | - | L | ST1C | BPCS | DCS | - | - | - | - | - | 214359C-6602-PID-0021-0219 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 7 | 660F5390 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | EXT_230V | NR | - | - | - | - | - | - | - | - | - | 660BJM537/P24 | - | E10202* | - | - | - | - | - | - | - | - | - | N/A | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660ZE5500A | - | 660K5001 - MACHINE PROTECTION SYSTEM | AXIAL DISPLACEMENT | - | - | - | - | - | L | - | MAINT | - | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm HH: 0.4 Alarm H: 0.35 | - | - | - | 2 | 660Z5500 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.25 | mm | - | 2.3 | mm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660ZE5500B | - | 660K5001 - MACHINE PROTECTION SYSTEM | AXIAL DISPLACEMENT | - | - | - | - | - | L | - | MAINT | - | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm HH: 0.4 Alarm H: 0.35 | - | - | - | 2 | 660Z5500 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0.25 | mm | - | 2.3 | mm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660ZT5501B | - | 660K5001 - MACHINE PROTECTION SYSTEM | AXIAL DISPLACEMEN | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -1 | 1 | ALERT (0,3mm) / Shutdown (0,4mm) | mm | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660Z5501 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -1 | mm | - | 1 | mm | - | - | - | - | - | - | AI20 | - | - | - | - | - | - | - | - | - | - | - | 660BJIMS525/P02 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 1 | - | 660ZT5502A | - | 660K5001 - MACHINE PROTECTION SYSTEM | AXIAL DISPLACEMEN | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -1 | 1 | ALERT (0,3mm) / Shutdown (0,4mm) | mm | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660Z5502 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -1 | mm | - | 1 | mm | - | - | - | - | - | - | AI20 | - | - | - | - | - | - | - | - | - | - | - | 660BJIMS525/P03 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660ZI5500 | - | 660K5001 - MACHINE PROTECTION SYSTEM | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660Z5500 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660ZAH5500 | - | 660K5001 - MACHINE PROTECTION SYSTEM | ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660Z5500 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660ZE5501A | - | 660K5001 - MACHINE PROTECTION SYSTEM | AXIAL DISPLACEMENT | - | - | - | - | - | L | - | MAINT | - | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm HH: 0.4 Alarm H: 0.3 | - | - | - | 2 | 660Z5501 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -1 | mm | - | 1 | mm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660ZE5501B | - | 660K5001 - MACHINE PROTECTION SYSTEM | AXIAL DISPLACEMENT | - | - | - | - | - | L | - | MAINT | - | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm HH: 0.4 Alarm H: 0.3 | - | - | - | 2 | 660Z5501 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -1 | mm | - | 1 | mm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XTS5513 | - | 660K5001 - MACHINE PROTECTION SYSTEM | VIBRATION | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 150 | ALERT (61,8μm) / Shutdown (71,3μm) | μm | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660X5513 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | µm | - | 150 | µm | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS525/P10 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XTS5514 | - | 660K5001 - MACHINE PROTECTION SYSTEM | VIBRATION | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 150 | ALERT (61,8μm) / Shutdown (71,3μm) | μm | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660X5514 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | µm | - | 150 | µm | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS525/P11 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660ZI5501 | - | 660K5001 - MACHINE PROTECTION SYSTEM | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660Z5501 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660ZAH5501 | - | 660K5001 - MACHINE PROTECTION SYSTEM | ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660Z5501 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 1 | - | 660ZS5501 | - | COMP F AXIAL HH | CONTACT | - | - | NORMALLY CLOSE | N | - | ITR | ST1D | MAINT | S-PLC | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | FROM ST1C / MMS | - | - | - | 7 | 660Z5501 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | N/A | - | By OSBL | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660ZE5502A | - | 660K5001 - MACHINE PROTECTION SYSTEM | AXIAL DISPLACEMENT | - | - | - | - | - | L | - | MAINT | - | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm HH: 0.4 Alarm H: 0.3 | - | - | - | 2 | 660Z5502 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -1 | mm | - | 1 | mm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660ZE5502B | - | 660K5001 - MACHINE PROTECTION SYSTEM | AXIAL DISPLACEMENT | - | - | - | - | - | L | - | MAINT | - | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | Alarm HH: 0.4 Alarm H: 0.3 | - | - | - | 2 | 660Z5502 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -1 | mm | - | 1 | mm | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 1 | - | 660XTS5515 | - | 660K5001 - MACHINE PROTECTION SYSTEM | VIBRATION | - | - | - | N | - | L | ST1C | MAINT | MMS | - | 0 | 150 | ALERT (61,8μm) / Shutdown (71,3μm) | μm | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660X5515 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 0 | µm | - | 150 | µm | - | - | - | - | - | - | AI20 | - | - | - | - | - | - | - | - | - | - | - | 660BJIMS525/P12 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 1 | - | 660ZT5502B | - | 660K5001 - MACHINE PROTECTION SYSTEM | AXIAL DISPLACEMEN | - | - | - | N | - | L | ST1C | MAINT | MMS | - | -1 | 1 | ALERT (0,3mm) / Shutdown (0,4mm) | mm | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 3 | 660Z5502 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -1 | mm | - | 1 | mm | - | - | - | - | - | - | AI20 | - | - | - | - | - | - | - | - | - | - | - | 660BJIMS525/P04 | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 1 | - | 660ZI5502 | - | 660K5001 - MACHINE PROTECTION SYSTEM | INDICATION | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 5 | 660Z5502 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 1 | - | 660ZAH5502 | - | 660K5001 - MACHINE PROTECTION SYSTEM | ALARM | - | - | - | N | - | CRD | SdC | MAINT | DCS | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | - | - | - | - | 8 | 660Z5502 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 1 | - | 660ZS5502 | - | COMP M AXIAL HH | CONTACT | - | - | NORMALLY CLOSE | N | - | ITR | ST1D | MAINT | S-PLC | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | FROM ST1C / MMS | - | - | - | 7 | 660Z5502 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | N/A | - | By OSBL | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660ZS5505 | - | GB LS AXIAL HH | CONTACT | - | - | NORMALLY CLOSE | N | - | ITR | ST1D | MAINT | S-PLC | - | - | - | - | - | P22201-100-03 | - | - | - | - | 660-2-Fractionation | FROM ST1C / MMS | - | - | - | 7 | 660Z5505 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | N/A | - | NO | - | NI (NOT INSULATED) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | NR | - | - | - | - | - | - | - | - | - | N/A | - | By OSBL | - | - | - | - | - | - | - | - | - | HOLD | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660ZT5509 | - | 660G5001A-SHAFT AXIAL DISPLACEMENT (ACCELEROMETER) | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | GEARBOX OR PUMP | - | - | - | 3 | 660Z5509 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660ZTS5510 | - | 660G5001A-SHAFT AXIAL DISPLACEMENT (ACCELEROMETER) | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | GEARBOX OR PUMP | - | - | - | 3 | 660Z5510 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660ZTS5511 | - | 660G5001B-SHAFT AXIAL DISPLACEMENT (ACCELEROMETER) | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | GEARBOX OR PUMP | - | - | - | 3 | 660Z5511 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660ZT5512 | - | 660G5001B-SHAFT AXIAL DISPLACEMENT (ACCELEROMETER) | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | - | - | - | - | FR-GPS-100-0-FLOW-002119 | - | - | - | - | 660-2-Fractionation | GEARBOX OR PUMP | - | - | - | 3 | 660Z5512 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660ZTS5513 | - | 660G5002A-SHAFT AXIAL DISPLACEMENT (ACCELEROMETER) | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | - | - | - | - | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | GEARBOX OR PUMP | - | - | - | 3 | 660Z5513 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660ZTS5514 | - | 660G5002B-SHAFT AXIAL DISPLACEMENT (ACCELEROMETER) | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | - | - | - | - | FR-GPS-100-0-FLOW-002120 | - | - | - | - | 660-2-Fractionation | GEARBOX OR PUMP | - | - | - | 3 | 660Z5514 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660ZTS5515 | - | 660G5003A-SHAFT AXIAL DISPLACEMENT (ACCELEROMETER) | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | - | - | - | - | FR-GPS-100-0-FLOW-002121 | - | - | - | - | 660-2-Fractionation | GEARBOX OR PUMP | - | - | - | 3 | 660Z5515 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 1 | - | 660ZTS5516 | - | 660G5003B-SHAFT AXIAL DISPLACEMENT (ACCELEROMETER) | ACCELEROMETER | - | - | - | N | - | L | ST1C | MAINT | MMS | - | - | - | - | - | FR-GPS-100-0-FLOW-002121 | - | - | - | - | 660-2-Fractionation | GEARBOX OR PUMP | - | - | - | 3 | 660Z5516 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | ATEX | - | - | - | - | - | - | - | - | - | - | -
Note on W7: Joan Bofill-Cardona: This data will be updated automatically when the SP is done. For Speed control range shall be manually.
Note on X7: Joan Bofill-Cardona: This data will be updated automatically when the SP is done. For Speed control range shall be manually.
Note on AL7: Joan Bofill-Cardona: This data will be updated automatically when the SP is done
Note on BZ7: Joan Bofill-Cardona: Instrument range (All Span)
Note on CG7: Joan Bofill-Cardona: Instrument range (All Span)
Note on CI7: Joan Bofill-Cardona: Calibration of Instrument
Note on CJ7: Joan Bofill-Cardona: Calibration of Instrument
Note on FT9: Paulo-Gilberto Martins-Afonso-External: 0 Meaning
Note on FU9: Paulo-Gilberto Martins-Afonso-External: 0 Meaning
Note on FV9: Paulo-Gilberto Martins-Afonso-External: 0 Meaning
Note on FW9: Paulo-Gilberto Martins-Afonso-External: 0 Meaning
Note on I12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The Tag has been changed to add the _S_ according to the TTE/STD.
Note on I13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The Tag has been changed to add the _S_ according to the TTE/STD.
Note on I14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The Tag has been changed to add the _S_ according to the TTE/STD. Will be changed in the 660_1 wiring diagram.
Note on I15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The Tag has been changed to add the _S_ according to the TTE/STD.
Note on DC15: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Pair connection was assigned wrong (660BJGS532/T05), we modified to be match the JB wiring diagram (660BJGS532/T03)
Note on I16: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The Tag has been changed to add the _S_ according to the TTE/STD.
Note on I17: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The Tag has been changed to add the _S_ according to the TTE/STD.
Note on I18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The Tag has been changed to add the _S_ according to the TTE/STD.
Note on I19: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The Tag has been changed to add the _S_ according to the TTE/STD.
Note on I20: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The Tag has been changed to add the _S_ according to the TTE/STD.
Note on I21: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The Tag has been changed to add the _S_ according to the TTE/STD.
Note on I22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The Tag has been changed to add the _S_ according to the TTE/STD.
Note on DC22: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Pair connection was assigned wrong (660BJGS532/T06), we modified to be match the JB wiring diagram (660BJGS532/T04)
Note on I23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The Tag has been changed to add the _S_ according to the TTE/STD.
Note on DC23: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Pair connection was assigned wrong (660BJGS532/T07), we modified to be match the JB wiring diagram (660BJGS532/T05)
Note on I24: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The Tag has been changed to add the _S_ according to the TTE/STD.
Note on I25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The Tag has been changed to add the _S_ according to the TTE/STD.
Note on I26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The Tag has been changed to add the _S_ according to the TTE/STD.
Note on I27: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The Tag has been changed to add the _S_ according to the TTE/STD.
Note on DC27: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Pair connection was assigned wrong (660BJGS532/T08), we modified to be match the JB wiring diagram (660BJGS532/T06)
Note on I28: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The Tag has been changed to add the _S_ according to the TTE/STD.
Note on DC28: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Pair connection was assigned wrong (660BJGS532/T09), we modified to be match the JB wiring diagram (660BJGS532/T07)
Note on I29: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Signal has been deleted according to the cost saving modification
Note on DC29: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Pair connection was assigned wrong (660BJGS532/T03), we modified to be match the JB wiring diagram (660BJGS532/T08) - Signa has been deleted based on the cost saving
Note on I30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The Tag has been changed to add the _S_ according to the TTE/STD.
Note on DC30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Pair connection was assigned wrong (660BJGS532/T04), we modified to be match the JB wiring diagram (660BJGS532/T09)
Note on I31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The Tag has been changed to add the _S_ according to the TTE/STD. Will be changed in the 660_1 wiring diagram.
Note on I32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The Tag has been changed to add the _S_ according to the TTE/STD.
Note on I33: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The Tag has been changed to add the _S_ according to the TTE/STD.
Note on I34: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: New signal has been added
Note on DC34: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: HB has been assigned to the new signal
Note on I35: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Signal has been deleted according to the cost saving modification
Note on DC35: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Signal has been deleted based on the cost saving
Note on I36: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The Tag has been changed to add the _S_ according to the TTE/STD.
Note on I37: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag was assigned wrong(660TI5330), the correct tag is (660TT5330)
Note on I38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag was assigned wrong(660TI5330), the correct tag is (660TT5330)
Note on DC38: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The Pair assigned was wrong (/P15), the correct pair is / P16.
Note on DC39: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The Pair assigned was wrong (/P16), the correct pair is / P17.
Note on DC80: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: TB was assigned wrong, the correct TB is 660BJMSP05
Note on DC81: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: TB was assigned wrong, the correct TB is 660BJMSP06
Note on DC148: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: TB was assigned wrong, the correct TB is 660BJMSP08
Note on DC152: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: TB was assigned wrong, the correct TB is 660BJMSP08
Note on DC191: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The Junction box has been changed from 660BJMS102/09 to the Junction box 660BJMS155/P11.
Note on DC200: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The Junction box has been changed from 660BJMS102/09 to the Junction box 660BJMS155/P11.
Note on I1304: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Tag was assigned wrong (660PT5415), the correct tag is 660PT5215
Note on DC1550: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Pair connection point has been added (pair 23).
Note on DC1597: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Pair connection point has been added (pair 24).
Note on DC1881: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: JB tag was missing, the assigned JB is 660BJMS502/P18
Note on DC1901: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: JB tag was assigned wrong, the correct assigned JB is 660BJMS502/P19
Note on DC1902: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: JB tag was missing, the assigned JB is 660BJMS502/P20
Note on DC1914: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: JB tag was assigned wrong, the correct assigned JB is 660BJMS502/P21
Note on DC1915: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: JB tag was assigned wrong, the correct assigned JB is 660BJMS502/P19
Note on I2079: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The signal is not indicated on the last update vendor documentation, the signal assigned has been deleted
Note on DC2079: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The signal is not indicated on the last update vendor documentation, the JB assigned (660LP530/TS3-C35-C36) has been deleted

## Notes
Note:1
| Note:2 | Note:3
Note:4 | Note:5 | Note:6