## IO_LIST
[5 empty] | Project n° | Unit | Document code | Material Code | Serial n° | Rev. | Page
[5 empty] | 214359C | 6603 | NM | 1511 | 0001 | 0 | Page 08 of 10
LPG Recovery- CONFIGURATION IO LIST
ISBL (TEN )/ OSBL (ARTELIA) SCOPE |  | ISBL | ISBL | ISBL |  | ISBL | ISBL | ISBL | ISBL | ISBL | ISBL |  |  | ISBL | ISBL |  | ISBL | ISBL | ISBL | ISBL | OSBL | ISBL | ISBL | ISBL | ISBL | ISBL | OSBL | ISBL | ISBL | ISBL | ISBL | ISBL |  | ISBL |  | ISBL | ISBL | ISBL | ISBL |  |  |  |  | ISBL | N/A | ISBL | ISBL | ISBL | ISBL | N/A | ISBL | ISBL | N/A | ISBL | ISBL | ISBL | ISBL | RP | RP | ISBL | ISBL | RP/INSP | RP/INSP | RP/INSP |  |  |  |  | ISBL | ISBL | ISBL | ISBL | ISBL | ISBL |  | ISBL | ISBL | ISBL | ISBL | ISBL | ISBL |  |  |  |  | OSBL | ISBL | ISBL | ISBL/OSBL |  | ISBL | OSBL | ISBL/OSBL | OSBL | OSBL | OSBL | OSBL | OSBL | ISBL | ISBL | ISBL | ISBL | OSBL | ISBL/OSBL |  |  | ISBL |  |  |  | ISBL | ISBL | ISBL | ISBL | ISBL | ISBL |  |  |  |  | ISBL | ISBL | ISBL | ISBL | RP/INSP | ISBL | ISBL | ISBL | ISBL | [7 empty] | ISBL | [9 empty] | OSBL | OSBL | OSBL | OSBL | OSBL | OSBL | OSBL | OSBL | OSBL | OSBL | OSBL | OSBL | OSBL | OSBL | OSBL | OSBL | OSBL |  |  |  | ISBL | ISBL
Doc_Revision to be applied |  | IFD1 | IFD1 | IFD1 | N/A | IFD1 | IFD2 | IFD1 | IFD1 | IFD1 | IFD1 | N/A | N/A | IFD1 | IFD1 | N/A | IFD1 | IFD1 | IFD1 | IFD1 | N/A | IFD2 | IFD2 | IFD3 | IFD2 | IFD1 | N/A | N/A | N/A |  | IFD1 | IFD1 |  | IFD1 (Chk by Nohora) |  | IFD1 | IFD2 | IFD1 | IFD1 |  |  |  |  | IFD3 |  | IFD3 | IFD3 | IFD3 | IFD3 |  | IFD3 |  | IFD3 | IFD3 | IFD3 | IFD3 | IFD3 by SIL Man | N/A | N/A | IFD3 by SIL Man | IFD3 by SIL Man | N/A | N/A | N/A | N/A | N/A | N/A | N/A | IFD1 chk by EDG | IFD1 chk by EDG | IFD1 chk by EDG | IFD1 chk by EDG | IFD1 chk by EDG | IFD1 chk by EDG |  | IFD2 | IFD2 | IFD2 | IFD2 | IFD2 | IFD2 | N/A | N/A | N/A | N/A | N/A | IFD1 | IFD1 | IFD1 | N/A | IFD1 | N/A | IFD2 | N/A | N/A | N/A | N/A | N/A | IFD2 |  | IFD2 | IFD3 | N/A | IFD2 | N/A | N/A | IFD3 | N/A | N/A | N/A | IFD2 | IFD2 | IFD2 | IFD2 | IFD2 | IFD2 | N/A | N/A | N/A | N/A | IFD3 - Only aplycable for Safety On-Off Valves with Air Tank |  |  |  | N/A | IFD2 | IFD2 | IFD2 | IFD2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | IFD2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | IFD3 | IFD3
| N° typical loop | 214359C-000-PID-0090-000x |  |  | Desciption typical loop | REV | Id. | TAG | OLD_TAG | SERVICE | FUNCTION | FUNCTION | SPI Process_Function | SUB_FUNCTION | METROLOG | METROLOG_DB_REF | LOC | NAME_LOC | LOOP_TYPE | SYSTEM | NUM | RANGE_MIN | RANGE_MAX | THRES_VALUE | RANGE & THRES. UNIT | PID | OPERGRAPH | CONT_DIAGRAM (9R) | LOGIG_DIAGRAM (9S) | FUNC_LOOP | PLANT UNIT | OBS_GEN | OBS_RAF | ANALYSER_TYPE | FUT_SPEC_03 | RG | LOOP | MOD | MOD_OBS | OBS_PRJ | FUT_SPEC_04 | FUT_SPEC_05 | FUT_SPEC_06 | DOC_HAZOP | DOC_SIL | DOC_SIF | SIF_1 | SIF_X | SIL_LEVEL | AIL_LEVEL | FALLBACK_POSITION | FAIL POSITION SPI | FAILSAFE | SRC | SRC_DESC | S_TYPE | PST | TEST_PROC_NUMBER | TEST_TYPE | T1 | MTTR | COCL | COCL_DESC | COCL_VALUE | OBS_SIS | FUT_SPEC_07 | FUT_SPEC_08 | FUT_SPEC_09 | HOOK_UP | INS | HEAT | HEAT_TYPE | INSULATION | HEAT_INSULATION_STD | BUFFER_LIQ | CAL_MIN_EQU | CAL_MAX_EQU | UN_CAL | REG_MIN_EQU | REG_MAX_EQU | UN_REG | GPS | ACC | OBS_INS | FUT_SPEC_12 | SEND_TO | SIG | ALIM | ISOLATOR | LIGHTNING | DUPLICATOR | I/O_CARD_TYPE | MARSH_CABINET | SYSTEM_CABINET | SEC | RACK | SLOT | I/O_ADDRESS | JB_TAG | JB_SPI_TAG | ELECTRICAL_H-UP | AIR_MANIFOLD | LOOP_DWG | JB_DWG | NET_TYPE | NET_DB_REF | OBS_WIR | FUT_SPEC_13 | FUT_SPEC_14 | FUT_SPEC_15 | FLUID | LGS | P_SER | P_MAX | T_SER | T_MAX | OBS_PRO | FUT_SPEC_16 | FUT_SPEC_17 | FUT_SPEC_18 | PED | VOL_PED | PED_CAT | PED_MODULE | PED_SAFE_EQU | A_C_S | ATEX_ZONE | ATEX_GAS_ZONE | ATEX_TEMP_ZONE | ATEX_CERT | ATEX_CE_NUMBER | DOC_ATEX | OBS_REG | FUT_SPEC_19 | FUT_SPEC_20 | FUT_SPEC_21 | DATA_SHEET | DATE_SERV | CTG_CODE | SAP_LINK | PLANT_NUMBER | SECTION_RAF | OBS_SUP | FUT_SPEC_22 | FUT_SPEC_23 | FUT_SPEC_24 | PRIORITY | BYP | AL_ACT | AL_IND | AL_EQUA | DESC_AL_EQUA | BUNDLED | MSK_GSD | MSK_SD | MSK_EQUIP | MSK_START | MSK_PERTU | MSK_AL_EQUA | DESC_MSK_AL_EQUA | MSK_1DEF | ALARM_REM | OBS_ALA | FUT_SPEC_25 | FUT_SPEC_26 | FUT_SPEC_27 | "0" Word | "1" Word | RAF_01 | RAF_02 | RAF_03 | RAF_04 | RAF_05 | RAF_06 | RAF_07 | RAF_08 | RAF_09 | RAF_10 | RAF_11 | RAF_12 | RAF_13 | RAF_14 | RAF_15 | RAF_16 | RAF_17 | RAF_18 | RAF_19 | RAF_20 | RAF_21 | RAF_22 | RAF_23 | RAF_24 | RAF_25 | RAF_26 | RAF_27 | RAF_28 | RAF_29 | RAF_30 | RAF_31 | RAF_32 | RAF_33 | RAF_34 | RAF_35 | RAF_36 | RAF_37 | RAF_38 | RAF_39 | RAF_40 | PROJ_01 | PROJ_02 | PROJ_03 | PROJ_04 | PROJ_05 | PROJ_06 | PROJ_07 | PROJ_08 | PROJ_09 | PROJ_10 | PROJ_11 | PROJ_12 | PROJ_13 | PROJ_14 | PROJ_15 | PROJ_16 | PROJ_17 | PROJ_18 | PROJ_19 | PROJ_20 | PROJ_21 | PROJ_22 | PROJ_23 | PROJ_24
- | - | - | - | 1 | - | 0 | - | 660AA4001A | - | Fault Analyzer | ALARM | - | - | - | - | - | AS | ST1C | BPCS | DCS | - |  |  | - |  | 214359C-6620-PID-0021-0308 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NI12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 18 | - | 0 | - | 660AA4001C | - | Fast Loop Low Flow | ALARM | - | - | - | - | - | AS | ST1C | BPCS | DCS | - |  |  | 500 | NL/h | 214359C-6620-PID-0021-0308 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NI12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 19 | - | 0 | - | 660AA4001D | - | Fault Low Flow | ALARM | - | - | - | - | - | AS | ST1C | BPCS | DCS | - |  |  | 4 | NL/h | 214359C-6620-PID-0021-0308 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NI12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660AA4002 | - | FROM 660-D-4003 | ALARM | - | - | - | - | - | L | ST1C | BPCS | DCS | - |  |  | 10 | NL/h | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4002 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | S | - | - | - | - | - | - | 660BJAN422/P02 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660AAH4002 | - | FROM 660-D-4003 | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 9.2 | ppm (mol) | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4002 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660AA4003A | - | Fault Analyzer | ALARM | - | - | - | - | - | AS | ST1C | BPCS | DCS | - |  |  | - |  | 214359C-6620-PID-0021-0308 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NI12 | - | - | - | - | S | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660AA4003B | - | Fault Purge | ALARM | - | - | - | - | - | AS | ST1C | BPCS | DCS | - |  |  | - |  | 214359C-6620-PID-0021-0308 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | S | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660AA4003C | - | Fast Loop Low Flow | ALARM | - | - | - | - | - | AS | ST1C | BPCS | DCS | - |  |  | 340 | NL/h | 214359C-6620-PID-0021-0308 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NI12 | - | - | - | - | S | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 0 | - | 660AA4003D | - | Fault Low Flow | ALARM | - | - | - | - | - | AS | ST1C | BPCS | DCS | - |  |  | 4 | NL/h | 214359C-6620-PID-0021-0308 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NI12 | - | - | - | - | S | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660FAL4500 | - | 660-D-4009 | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 0 | V | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4500 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 9 | - | 0 | - | 660XA4001A | - | 660 G 4001A ELEC FAULT | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | - |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4001A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 10 | - | 0 | - | 660XA4001AD | - | 660 G 4001A DISC SECU | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  | - |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4001A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 9 | - | 0 | - | 660XA4001B | - | 660 G 4001B ELEC FAULT | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | - |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4001B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 10 | - | 0 | - | 660XA4001BD | - | 660 G 4001B DISC SECU | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  | - |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4001B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 10 | - | 0 | - | 660XA4002 | - | 660 G 4002 ELEC FAULT | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | - |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4002 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 11 | - | 0 | - | 660XA4002D | - | 660 G 4002 DISC SECU | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  | - |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4002 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 10 | - | 0 | - | 660XA4003 | - | 660 G 4003 ELEC FAULT | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | - |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 11 | - | 0 | - | 660XA4003D | - | 660 G 4003 DISC SECU | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  | - |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 9 | - | 0 | - | 660XA4004 | - | 660 G 4004 ELEC FAULT | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | - |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4004 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 10 | - | 0 | - | 660XA4004D | - | 660 G 4004 DISC SECU | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  | - |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4004 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 10 | - | 0 | - | 660XA4005A | - | 660 G 4005A ELEC FAULT | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | - |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4005A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 11 | - | 0 | - | 660XA4005AD | - | 660 G 4005A DISC SECU | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  | - |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4005A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 10 | - | 0 | - | 660XA4005B | - | 660 G 4005B ELEC FAULT | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | - |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4005B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 11 | - | 0 | - | 660XA4005BD | - | 660 G 4005B DISC SECU | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  | - |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4005B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 7 | - | 0 | - | 660XA4006A | - | 660 G 4006A ELEC FAULT | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | - |  | FR-GPS-100-0-OMG-000003 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4006A | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 8 | - | 0 | - | 660XA4006AD | - | 660 G 4006A DISC SECU | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  | - |  | FR-GPS-100-0-OMG-000003 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4006A | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 7 | - | 0 | - | 660XA4006B | - | 660 G 4006B ELEC FAULT | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | - |  | FR-GPS-100-0-OMG-000003 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4006B | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 8 | - | 0 | - | 660XA4006BD | - | 660 G 4006B DISC SECU | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  | - |  | FR-GPS-100-0-OMG-000003 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4006B | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660HSA4010 | - | LPG UNIT ISOLATION AND DEPRESSURIZATION | ALARM | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  | - |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4010 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660HSA4011 | - | COMPRESSOR CIRCUIT ISOLATION AND DEPRESSURIZATION | ALARM | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  | - |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4011 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660HSA4012 | - | COMPRESSOR CIRCUIT ISOLATION | ALARM | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  | - |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4012 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660HSA4014 | - | LPG CIRCUIT ISOLATION | ALARM | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  | - |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4014 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660HSA4015 | - | LPG CIRCUIT ISOLATION | ALARM | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  | - |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4015 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660HA4020 | - | 660-K-4001 FIRST STAGE | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | - |  | 214359C-6603-PID-0021-0402 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4020 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660HSA4021 | - | LPG PRODUCT PUMPS SHUTDOWN | ALARM | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  | - |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4021 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 9 | - | 0 | - | 660XAK4001 | - | 660 KM 4001 ELEC FAULT | ALARM | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - |  |  | - |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660K4001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 10 | - | 0 | - | 660XAK4001D | - | 660 KM 4001 DISC SECU | ALARM | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  | - |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660K4001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 15 | - | 0 | - | 660LAX4020 | - | 660-D-4001 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | N/A | mm | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4020 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 17 | - | 0 | - | 660LAX4023 | - | 660-D-4002 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | N/A |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4023 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 17 | - | 0 | - | 660LAX4026 | - | 60-D-4003 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | - |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4026 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 29 | - | 0 | - | 660XA4026A | - | 60-D-4003 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  | - |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4026 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 30 | - | 0 | - | 660XA4026B | - | 60-D-4003 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  | - |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4026 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 17 | - | 0 | - | 660LAX4033 | - | 660-D-4004 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | - |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4033 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 17 | - | 0 | - | 660LAX4034 | - | 660-D-4004 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | - |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4034 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660LDAX4039 | - | 660 D 4005 | ALARM | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  | - |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4039 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660LDAX4052 | - | 660D4004 | ALARM | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  | - |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4052 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660LSL4500A | - | 660-D-4009 | SOFT THERSHOLD | - | - | - | - | - | ITR | ST1D | SIS | S-PLC | - |  |  | 8 | mA | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4500 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660LSL4500B | - | 660-D-4009 | SOFT THERSHOLD | - | - | - | - | - | ITR | ST1D | SIS | S-PLC | - |  |  | 8 | mA | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4500 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660LSL4502 | - | 660-E-4006 | SOFT THERSHOLD | - | - | - | - | - | ITR | ST1D | SIS | S-PLC | - |  |  | 8 | mA | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4502 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660PAX4221 | - | HDT PURGE FROM 662C3001 | ALARM | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  | - |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4221 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 17 | - | 0 | - | 660PAX4320 | - | 660-D-4001 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | - |  | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4320 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 13 | - | 0 | - | 660PAX4332 | - | 660-D-4001 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | - |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4332 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 11 | - | 0 | - | 660PAX4333 | - | 660-D-4001 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | - |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4333 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660PAX4335 | - | Off Gas From 660-D-4004 To 660-D-4001 | ALARM | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  | - |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4335 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 13 | - | 0 | - | 660PAX4336 | - | 660-D-4001 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | - |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4336 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 11 | - | 0 | - | 660PAX4337 | - | 660-D-4001 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | - |  | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4337 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660PAX4342 | - | 660 D 4006 | ALARM | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  | - |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4342 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 13 | - | 0 | - | 660PAX4504 | - | 660-G-4002 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | - |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4504 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 13 | - | 0 | - | 660PAX4515 | - | FROM 660-E-4007A/B | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | - |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4515 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 13 | - | 0 | - | 660PAX4526 | - | Leakage Gas | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | - |  | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4526 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 17 | - | 0 | - | 660TAX4130 | - | 660-D-4001 | ALARM | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  | - |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4130 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 17 | - | 0 | - | 660TAX4132 | - | 660-D-4001 | ALARM | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  | - |  | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4132 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 0 | - | 660TAX4143 | - | OFF GAS TO SMR | ALARM | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  | - |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4143 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 5 | - | 0 | - | 660XA4155 | - | FROM 660-D-4001 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  | - |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4155 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 6 | - | 0 | - | 660XA4156 | - | FROM 660-D-4001 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  | - |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4156 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 6 | - | 0 | - | 660XA4157 | - | FROM 660-D-4001 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  | - |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4157 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 7 | - | 0 | - | 660XA4159 | - | FROM 660-D-4002 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  | - |  | 214359C-6603-PID-0021-0404 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4159 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 5 | - | 0 | - | 660XA4160D | - | FROM 660-D-4003 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  | - |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4160 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 6 | - | 0 | - | 660XA4161 | - | FROM 660-D-4003 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  | - |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4161 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 6 | - | 0 | - | 660XA4162 | - | LPG TO BATTERY LIMITS | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  | - |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4162 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 6 | - | 0 | - | 660XA4163 | - | FROM 660-D-4003 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  | - |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4163 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 6 | - | 0 | - | 660XA4164 | - | LPG FROM 660 G 4001 A/B | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  | - |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4164 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 5 | - | 0 | - | 660XA4165D | - | LPG Dryer depressuring | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  | - |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4165 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 6 | - | 0 | - | 660XA4166 | - | TO SWS | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  | - |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4166 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 6 | - | 0 | - | 660XA4167 | - | LPG TO 660 G 4001 A/B | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  | - |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4167 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 6 | - | 0 | - | 660XA4168 | - | Brine to LPG Dryer Recovery drum | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  | - |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4168 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 6 | - | 0 | - | 660XA4169 | - | FROM 660-D-4003 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  | - |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4169 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 6 | - | 0 | - | 660XA4170 | - | FROM 660-D-4003 | ALARM | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - |  |  | - |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4170 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV07 | - | 6 | - | 0 | - | 660XA4222 | - | LP STEAM TO 660E4004 | ALARM | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - |  |  | - |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4222 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| Only for DB Typical | Valves & Motor typical GALAXIE Project (include in PID Legend) | Typical Control Schema GALAXIE Project | SPI Internal Loop Order GALAXIE Project | Only for DB Typical | [5 empty] | EN | FR | DE | EN | Y/N | File name | [7 empty] | CHECK SEUIL and ALARM EQUAL |  | File name | File name | File name | File name |  |  | Spare Observation if necessary | Spare Observation if necessary | [5 empty] | Spare Observation if necessary | Spare Observation if necessary |  |  |  | File name | File name | File name | [5 empty] | FIELD T.EN For Internal Checking | Y/N or empty |  |  |  |  | File name |  |  |  | Y/N or black |  |  | Spare Observation if necessary |  |  |  | File name |  |  |  |  | File name | [9 empty] | Spare Observation if necessary | [15 empty] | T.EN for Internal Checking | T-ELECTR H-UP |  | File name | File name |  | File name | [18 empty] | Y/N or empty | [7 empty] | Spare Observation if necessary | [9 empty] | Spare Observation if necessary | [10 empty] | Y/N or empty | Y/N or empty | [7 empty] | Spare Observation if necessary |  |  |  | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary | Spare Observation if necessary
[5 empty] | Description Ligne Desciption typical loop | Revision index of each record | Internal Id. SPI or AVEVA | TAG number of the function or equipment | Old TAG number | Service of the function or equipment | Type of equipment or function handled | Type of equipment or function handled |  | Sub function of the type of equipment. | Indicate if the equpment or processing system are tracked metrologically | Gives the name of the system database managing the metrological traking for equipment. | Location of the equipment or of the function handled | Common name for all locations | Loop type (control / safety / Maintenance) | System type of the processing system managing the function or equipment | Assigns a serial number to the processing system managing the function or equipment | Bottom value of display scale | Top value of the display scale | Threshold setting value | Unit of the display scale or physical unit | Number of the PID of the function or equipment | Number of the opergraph of the function or equipment | Control drawing number | Number of the safety or automation logic diagram | Functional loop name | Unit Name | Observations associated with the general fields | Observations | Analyser Type | Spare for specification GS RC INS 107 | Serial number of the record in the loop | Loop name | Modification type on instrument | Observations associated with the modification | Observations | Spare for specification GS RC INS 107 | Spare for specification GS RC INS 107 | Spare for specification GS RC INS 107 | HAZOP review document number (G-HSEQ-908) | SIL review document number (G-HSEQ-908) | SIF review document number (GS RC INS 150) | Assignment in the safety instrumented functions (GS RC INS 107 / GS RC INS 150) | Assignment in the safety instrumented functions (GS RC INS 107 / GS RC INS 150) | Integrity level of the equipment SIL (GS RC INS 600) | Integrity level of the equipment AIL (GS RC INS 600) | Fallback position for measuring instrument in case of his failure (GS RC INS 400) |  | Defines whether the equipment has a FAILSAFE mode (GS RC INS 400 / GS RC INS 450 / GS RC INS 451) | Safety regulation classification of the sensor or actuator depending country | Description of the SRC service | Origin of safety function covered (GS RC INS 100) | Process Safety Time (GS RC INS 451) | Safety test procedure for the function or equipment | Particular physical test device for the equipment | T1 (GS RC INS 600) | MTTR (GS RC INS 600) | Limit critical operating conditions | Description of the limit critical operating conditions | Physical values of the limit critical operating conditions | Observations associated with the safety fields | Spare for specification GS RC INS 107 | Spare for specification GS RC INS 107 | Spare for specification GS RC INS 107 | 1 | Instrument piping class (GS RC INS 200) | Instrument heat tracing type (GS RC INS 220) | Instrument heat tracing fluid (GS RC INS 220) | Instrument insulating type (GS RC INS 220) | Number of standard protection diagram (GS RC INS 220) | Type of buffer liquid between the sensor and the process fluid (GS RC INS 400) | Minimum instrument calibration range | Maximum instrument calibration range | Calibration unit for the instrument | Minimum Instrument setting | Minimum Instrument setting | Setting unit for the instrument (GS RC INS 400) | Geographic coordinates of the instrument (GS RC INS 150) | Instrument access means (GS RC INS 200) | Observations associated with the installation fields | Spare for specification GS RC INS 107 | Gives the end point for a link between systems | Nature of the signal for the inputs/outputs of an electrical/electronic/programmable electronic system or for exchanges between systems (GS RC INS 300 / GS RC INS 520 / GS RC INS 530) | Loop power supply (GS RC INS 300 / GS RC INS 520 / GS RC INS 530) | Type of isolator (GS RC INS 300 / GS RC INS 520 / GS RC INS 530) | Connection of a Lightning arrester to the instrument (GS RC INS 301) | Connection to signal duplicator (GS RC INS 810) | Type of I/O card where is linked the signal (GS RC INS 520 / GS RC INS 530) | Number of the connection cabinet for the instrument multicable (GS RC INS 105 / GS RC INS 300) | Number of the system cabinet (BPCS or SIS) where is linked the instrument (GS RC INS 105) | Assignment of the functional group in the oil unit or processing section in the digital control system | Number of the rack or face plate where is linked the instrument | Number of the rack or face plate where is linked the instrument | Number of the rack or face plate where is linked the instrument | Identifier of the junction box where is linked the instrument (GS RC INS 300 / GS RC INS 105) |  | Define the electrical material for Field Wiring | Identifier of the air distrubutor where is linked the instrument | Number of the loop drawing or troubleshooting drawing (GS RC INS 300 / GS RC INS 150) | Junction box drawing number (GS RC INS 300 / GS RC INS 150) | Gives the type of field bus network wired or wireless for the instrument | Gives the name of the system database managing the user network | Observations associated with the wirered fields | Spare for specification GS RC INS 107 | Spare for specification GS RC INS 107 | Spare for specification GS RC INS 107 | Fluid family in contact with the instrument (GS RC INS 200 / RG RC PVA 102) | State of the fluid in contact with the instrument (GS RC INS 107) | Pression de service du fluide (GS RC INS 107) | Pression maxi de service du fluide (GS RC INS 107) | Fluid operating temperature (GS RC INS 107) | Fluid Max operating temperature (GS RC INS 107) | Observations associated with the process fields | Spare for specification GS RC INS 107 | Spare for specification GS RC INS 107 | Spare for specification GS RC INS 107 | Spare for specification GS RC INS 107 | Volume of PED pressure chamber | PED category module | PED category module | PED safety accessory | Area Classification Standard. Standard or code classification for explosive atmosphere area | Type of ATEX ZONE where the instrument is located | ATEX gas group of the zone where the instrument is located | The most restrictive temperature class of the zone where the instrument is located | ATEX certificate of the instrument | Number of certificate of conformity | ATEX review document number | Observations associated with the regulatory fields | Spare for specification GS RC INS 107 | Spare for specification GS RC INS 107 | Spare for specification GS RC INS 107 | Number of the data sheet | Instrument start-up date | Instrument start-up date (DIGGR1600INS005) | SAP link for the instrument. | Instument code of the unit in the Refinery. | Section number of the refinery. | Observations associated with the supplier fields | Spare for specification GS RC INS 107 | Spare for specification GS RC INS 107 | Spare for specification GS RC INS 107 | Alarm priority (GS RC INS 502) | Type of maintenance bypass function associated with the alarm (GS RC INS 502) | Procedure to be followed to treat the alarm (GS RC INS 502) | Procedure to be followed when the alarm is unavailable (GS RC INS 502) | Equation generating the alarm (GS RC INS 502) | Equation description generating the alarm (GS RC INS 502) | Alarm group to which the alarm belongs (GS RC INS 502) | Assignment of the general shutdown masking for the alarm (GS RC INS 502) | Assignment of the unit shutdown masking for the alarm (GS RC INS 502) | Assignment of the equipment masking on shutdown for the alarm (GS RC INS 502) | Assignment of the unit start up masking for the alarm (GS RC INS 502) | Assignment of the unit disturbed operation masking for the alarm (GS RC INS 502) | Individual masking equation of the alarm (GS RC INS 502) | Equation description of the individual masking alarming (GS RC INS 502) | Assignment of the first fault masking for the alarm (GS RC INS 502) | Observations associated with the alarm (GS RC INS 502) | Observations associated with the alarm fields | Spare for specification GS RC INS 107 | Spare for specification GS RC INS 107 | Spare for specification GS RC INS 107 |  |  | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for refinery use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use | Field dedicated for project use
- | - | - | - | 2 | - | 0 | - | 660ANY4001L | - | FUEL GAS TO SMR | INDICATION | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | 0 | 70 |  | % | 214359C-6620-PID-0021-0308 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NI12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660AN4001A | - | FROM 660-D-4003 | INDICATION | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | 0 | 0.5 |  | % | 214359C-6620-PID-0021-0308 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NI12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660AN4001B | - | FROM 660-D-4003 | INDICATION | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | 0 | 5 |  | %MOL | 214359C-6620-PID-0021-0308 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NI12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660AN4001C | - | FROM 660-D-4003 | INDICATION | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | 0 | 0.2 |  | % | 214359C-6620-PID-0021-0308 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NI12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 0 | - | 660AN4001D | - | FROM 660-D-4003 | INDICATION | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | 0 | 150 |  | ppm (mol) | 214359C-6620-PID-0021-0308 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NI12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 0 | - | 660AN4001E | - | FROM 660-D-4003 | INDICATION | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | 0 | 40 |  | % | 214359C-6620-PID-0021-0308 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NI12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 0 | - | 660AN4001F | - | FROM 660-D-4003 | INDICATION | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | 0 | 5 |  | % | 214359C-6620-PID-0021-0308 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NI12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 9 | - | 0 | - | 660AN4001G | - | FROM 660-D-4003 | INDICATION | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | 0 | 50 |  | % | 214359C-6620-PID-0021-0308 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NI12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 10 | - | 0 | - | 660AN4001H | - | FROM 660-D-4003 | INDICATION | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | 0 | 10 |  | % | 214359C-6620-PID-0021-0308 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NI12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 11 | - | 0 | - | 660AN4001J | - | FROM 660-D-4003 | INDICATION | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | 0 | 5 |  | % | 214359C-6620-PID-0021-0308 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NI12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 12 | - | 0 | - | 660AN4001K | - | FROM 660-D-4003 | INDICATION | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | 0 | 2 |  | % | 214359C-6620-PID-0021-0308 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NI12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 14 | - | 0 | - | 660ANY4001M | - | FROM 660-D-4003 | INDICATION | - | - | - | - | - | AS | ST1C | BPCS | DCS | - |  |  |  |  | 214359C-6620-PID-0021-0308 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NI12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 16 | - | 0 | - | 660AT4001 | - | FROM 660-D-4003 | CHROMATO | - | - | ALIM EXT | - | - | AS | ST1C | BPCS | DCS | - |  |  |  |  | 214359C-6620-PID-0021-0308 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 17 | - | 0 | - | 660AA4001B | - | Fault Purge | ALARM | - | - | - | - | - | AS | ST1C | BPCS | DCS | - |  |  | - |  | 214359C-6620-PID-0021-0308 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | S | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660AI4002 | - | FROM 660-D-4003 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - | 0 | 30 |  | ppm (mol) | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4002 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660AT4002 | - | FROM 660-D-4003 | H2S | - | - | ALIM EXT | - | - | L | ST1C | BPCS | DCS | - | 0 | 30 |  | ppm (mol) | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4002 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | EXT_230V | - | - | - | S | - | - | - | - | - | - | 660BJAN422/P01 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 0 | - | 660FSL4002A | - | FROM 660-D-4003 | FLOW SWITCH | - | - | - | - | - | L | ST1C | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4002 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | S | - | - | - | - | - | - | 660BJAN422/P03 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660AT4003 | - | FROM 660-E-4004 | CHROMATO | - | - | ALIM EXT | - | - | AS | ST1C | BPCS | DCS | - |  |  |  |  | 214359C-6620-PID-0021-0308 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 0 | - | 660AN4003A | - | FROM 660-D-4003 | INDICATION | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | 0 | 70 |  | % | 214359C-6620-PID-0021-0308 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NI12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 0 | - | 660AN4003B | - | FROM 660-D-4003 | INDICATION | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | 0 | 0.5 |  | % | 214359C-6620-PID-0021-0308 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NI12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 9 | - | 0 | - | 660AN4003C | - | FROM 660-D-4003 | INDICATION | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | 0 | 5 |  | % | 214359C-6620-PID-0021-0308 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NI12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 10 | - | 0 | - | 660AN4003D | - | FROM 660-D-4003 | INDICATION | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | 0 | 0.2 |  | % | 214359C-6620-PID-0021-0308 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NI12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 11 | - | 0 | - | 660AN4003E | - | FROM 660-D-4003 | INDICATION | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | 0 | 150 |  |  | 214359C-6620-PID-0021-0308 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NI12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 12 | - | 0 | - | 660AN4003F | - | FROM 660-D-4003 | INDICATION | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | 0 | 40 |  | % | 214359C-6620-PID-0021-0308 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NI12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 13 | - | 0 | - | 660AN4003G | - | FROM 660-D-4003 | INDICATION | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | 0 | 5 |  | % | 214359C-6620-PID-0021-0308 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NI12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 14 | - | 0 | - | 660AN4003H | - | FROM 660-D-4003 | INDICATION | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | 0 | 50 |  | % | 214359C-6620-PID-0021-0308 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NI12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 15 | - | 0 | - | 660AN4003J | - | FROM 660-D-4003 | INDICATION | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | 0 | 10 |  | % | 214359C-6620-PID-0021-0308 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NI12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 16 | - | 0 | - | 660AN4003K | - | FROM 660-D-4003 | INDICATION | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | 0 | 5 |  | % | 214359C-6620-PID-0021-0308 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NI12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 17 | - | 0 | - | 660ANY4003L | - | FROM 660-D-4003 | INDICATION | - | - | - | - | - | AS | ST1C | BPCS | DCS | - | 0 | 1 |  | % | 214359C-6620-PID-0021-0308 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NI12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 18 | - | 0 | - | 660ANY4003M | - | FROM 660-D-4003 | INDICATION | - | - | - | - | - | AS | ST1C | BPCS | DCS | - |  |  |  |  | 214359C-6620-PID-0021-0308 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660A4003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | NI12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660XS4006A | - | 660E4006 ENABLE/DISABLE | CDE TOR | - | - | - | - | - | ESS | ST1 | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660E4006 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660HLS4006 | - | 660E4006 STOP | TPL STOP | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660E4006 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660XS4006B | - | 660E4006 | CDE TOR | - | - | - | - | - | ESS | ST1 | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660E4006 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660XS4008 | - | 660E4008 ENABLE/DISABLE | CDE TOR | - | - | - | - | - | ESS | ST1 | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660E4008 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660HLS4008 | - | 660E4008 STOP | TPL STOP | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660E4008 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660XS4008B | - | 660E4008 FAILURE | CONTACT | - | - | - | - | - | ESS | ST1 | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660E4008 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660XS4009 | - | 660E4009 ENABLE/DISABLE | CDE TOR | - | - | - | - | - | ESS | ST1 | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660E4009 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660HLS4009 | - | 660E4009 STOP | TPL STOP | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660E4009 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660XS4009B | - | 660E4009 FAILURE | CONTACT | - | - | - | - | - | ESS | ST1 | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660E4009 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660FE4227 | - | LPG TO 660D4004 | ORIFICE | - | - | - | - | - | L | - | BPCS | - | - | 0 | 7.5 |  | m³/h | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4227 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660FT4227 | 660-FT -4227A | LPG TO 660D4004 | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 7.5 |  | m³/h | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4227 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJM401/P01 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660FI4227 | - | LPG TO 660D4004 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4227 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660FC4227 | - | LPG TO 660D4004 | CONTROLLER | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4227 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660FY4227 | - | LPG TO 660D4004 | SOFT CALCULATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4227 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | CV01 | - | 6 | - | 0 | - | 660FV4227 | - | LPG TO 660D4004 | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4227 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJM401/P02 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660FI4228 | - | LPG Product from LPG Dryer | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4228 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660FT4228A | - | LPG Product from LPG Dryer | PRESSURE DP | - | - | - | - | - | L | - | BPCS | - | - | 0 | 2 |  | m³/h | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4228 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660FT4228 | - | LPG Product from LPG Dryer | CORIOLIS | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 4050 |  | kg/h | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4228 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | EXT_230V | - | - | - | S | - | - | - | - | - | - | 660BJM402/P01 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660FT4228B | - | LPG Product from LPG Dryer | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 7.5 |  | m³/h | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4228 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660FE4230 | - | OFF GAS FROM 660-D-4003 | ORIFICE | - | - | - | - | - | L | - | BPCS | - | - | 0 | 3000 |  | kg/h | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4230 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660FI4230 | - | OFF GAS FROM 660-D-4003 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4230 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660FT4230 | - | OFF GAS FROM 660-D-4003 | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 3000 |  | kg/h | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4230 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM403/P01 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660FE4231 | - | Off Gas From HP LPG Separator | ORIFICE | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 214359C-6603-PID-0022-0001 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4231 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660FI4231 | - | Off Gas From HP LPG Separator | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0022-0001 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4231 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660FT4231 | - | Off Gas From HP LPG Separator | PRESSURE DP | - | - | - | - | - | L | - | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0022-0001 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4231 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660FE4233 | - | STEAM TO 660-E-4004 | ORIFICE | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4233 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660FT4233 | - | STEAM TO 660-E-4004 | VORTEX | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 100 |  | kg/h | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4233 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJM401/P10 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660FI4233 | - | STEAM TO 660-E-4004 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4233 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660FC4233 | - | STEAM TO 660-E-4004 | CONTROLLER | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4233 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | CV01 | - | 5 | - | 0 | - | 660FV4233 | - | STEAM TO 660-E-4004 | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4233 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJM401/P11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 0 | - | 660FY4233 | - | STEAM TO 660-E-4004 | SOFT CALCULATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4233 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660FI4236 | - | LPG TO 660D4004 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4236 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660FAL4236 | - | LPG TO 660D4004 | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 5.7 | m³/h | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4236 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660FT4236 | 660-FT -4227B | LPG TO 660D4004 | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 7.5 |  | m³/h | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4236 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM406/P14 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660FT4454 | - | METHANOL INJECTION PUMPS 660G4006B | FLOW TRANSMITTER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 100 |  | % | FR-GPS-100-0-OMG-000003 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4454 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 662BJM130/P22 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660FI4454 | - | METHANOL INJECTION PUMPS 660G4006A | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | FR-GPS-100-0-OMG-000003 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4454 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660FAL4454 | - | METHANOL INJECTION PUMPS 660G4006A | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | FR-GPS-100-0-OMG-000003 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4454 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660FAH4454 | - | METHANOL INJECTION PUMPS 660G4006B | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | FR-GPS-100-0-OMG-000003 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4454 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660FT4500 | - | 660-D-4009 | FLOW TRANSMITTER | - | - | - | - | - | L | ST1C | BPCS | DCS | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4500 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | EXT_24V | - | - | - | S | - | - | - | - | - | - | 660BJM456 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660FI4500 | - | 660-D-4009 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4500 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660FT4501 | - | 660-E-4005B | FLOW TRANSMITTER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 1.5 | 15 |  | m³/h | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4501 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM455/P03 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660FI4501 | - | 660-E-4005B | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4501 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660FAL4501 | - | 660-E-4005B | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 4.5 | m³/h | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4501 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660FT4502 | - | FROM 660E4007B | ROTAMETER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 1.5 | 15 |  | m³/h | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4502 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM455/P04 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660FI4502 | - | FROM 660E4007B | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4502 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660FAL4502 | - | FROM 660E4007B | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 4.5 | m³/h | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4502 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660FT4503 | - | TO 660D4010 | ROTAMETER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0.49 | 4.9 |  | m³/h | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4503 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM455/P05 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660FI4503 | - | TO 660D4010 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4503 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660FAL4503 | - | TO 660D4010 | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 1.20 | m³/h | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4503 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660FT4504 | - | TO 660D4010 | ROTAMETER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0.04 | 0.46 |  | m³/h | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4504 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM455/P06 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660FI4504 | - | TO 660D4010 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4504 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660FAL4504 | - | TO 660D4010 | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 0.12 | m³/h | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4504 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660FT4505 | - | TO 660D4010 | ROTAMETER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0.04 | 0.46 |  | m³/h | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4505 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM455/P07 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660FI4505 | - | TO 660D4010 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4505 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660FAL4505 | - | TO 660D4010 | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 0.12 | m³/h | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4505 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660FT4506 | - | TO 660D4010 | ROTAMETER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0.49 | 4.9 |  | m³/h | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4506 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM455/P08 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660FI4506 | - | TO 660D4010 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4506 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660FAL4506 | - | TO 660D4010 | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 1.25 | m³/h | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4506 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660FT4507 | - | Leakage Gas Distance Piece 2nd Stage | ROTAMETER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 4 | 40 |  | Nm³/h | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4507 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM455/P09 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660FI4507 | - | Leakage Gas Distance Piece 2nd Stage | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4507 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660FAH4507 | - | Leakage Gas Distance Piece 2nd Stage | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 31.5 | Nm³/h | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4507 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660FT4508 | - | Leakage Gas Distance Piece 1st Stage | ROTAMETER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 4 | 40 |  | Nm³/h | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4508 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM455/P010 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660FI4508 | - | Leakage Gas Distance Piece 1st Stage | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4508 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660FAH4508 | - | Leakage Gas Distance Piece 1st Stage | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 31.5 | Nm³/h | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4508 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660FT4509 | - | Leakage Gas Distance Piece 2nd Stage | ROTAMETER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 2.8 | 28 |  | Nm³/h | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4509 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM455/P11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660FI4509 | - | Leakage Gas Distance Piece 2nd Stage | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4509 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660FAH4509 | - | Leakage Gas Distance Piece 2nd Stage | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 22.5 | Nm³/h | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4509 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660FT4510 | - | Leakage Gas Distance Piece 1st Stage | ROTAMETER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 2.8 | 28 |  | Nm³/h | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4510 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM455/P12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660FI4510 | - | Leakage Gas Distance Piece 1st Stage | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4510 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660FAH4510 | - | Leakage Gas Distance Piece 1st Stage | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 22.5 | Nm³/h | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660F4510 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 1 | - | 0 | - | 660HS4001AD | - | 660 G 4001A LOCAL START | PB | - | - | NORMALLY OPEN | - | - | L | - | BPCS/SIS | MOT | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4001A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 2 | - | 0 | - | 660HSA4001AD | - | LPG FROM 660 D 4004 | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4001A | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 3 | - | 0 | - | 660HS4001AA | - | 660 G 4001A LOCAL ESD | ESD PB | - | - | NORMALLY CLOSE | - | - | L | - | BPCS/SIS | MOT | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4001A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 4 | - | 0 | - | 660HSA4001AA | - | LPG FROM 660 D 4004 | CONTACT | - | - | NORMALLY CLOSE | - | - | ESS | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4001A | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 5 | - | 0 | - | 660HLS4001A | - | 660 G 4001A STOP | TPL STOP | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4001A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 6 | - | 0 | - | 660HLS4001AA | - | 660 G 4001A TRIP | CDE TOR | - | - | NORMALLY CLOSE | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4001A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 7 | - | 0 | - | 660HLS4001AR | - | 660 G 4001A RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4001A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 8 | - | 0 | - | 660XS4001A | - | 660 G 4001A ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1C | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4001A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | S | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 11 | - | 0 | - | 660JT4001A | - | 660 G 4001A POWER MONITORING | POWER TRANSMITTER | - | - | - | - | - | ESS | ST1C | BPCS/SIS | DCS | - | 0 | 50 |  | Kw | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4001A | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | - | - | - | S | - | - | - | - | - | - | By OSBL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 12 | - | 0 | - | 660JI4001A | - | 660 G 4001A POWER MONITORING | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4001A | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 1 | - | 0 | - | 660HS4001BD | - | 660 G 4001B LOCAL START | PB | - | - | NORMALLY OPEN | - | - | L | - | BPCS/SIS | MOT | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4001B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 2 | - | 0 | - | 660HSA4001BD | - | LPG FROM 660 D 4004 | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4001B | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 3 | - | 0 | - | 660HS4001BA | - | 660 G 4001B LOCAL ESD | ESD PB | - | - | NORMALLY CLOSE | - | - | L | - | BPCS/SIS | MOT | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4001B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 4 | - | 0 | - | 660HSA4001BA | - | LPG FROM 660 D 4004 | CONTACT | - | - | NORMALLY CLOSE | - | - | ESS | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4001B | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 5 | - | 0 | - | 660HLS4001B | - | 660 G 4001B STOP | TPL STOP | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4001B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 6 | - | 0 | - | 660HLS4001BA | - | 660 G 4001B TRIP | CDE TOR | - | - | NORMALLY CLOSE | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4001B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 7 | - | 0 | - | 660HLS4001BR | - | 660 G 4001B RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4001B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 8 | - | 0 | - | 660XS4001B | - | 660 G 4001B ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1C | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4001B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | S | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 11 | - | 0 | - | 660JT4001B | - | 660 G 4001B POWER MONITORING | POWER TRANSMITTER | - | - | - | - | - | ESS | ST1C | BPCS/SIS | DCS | - | 0 | 50 |  | Kw | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4001B | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | - | - | - | S | - | - | - | - | - | - | By OSBL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 12 | - | 0 | - | 660JI4001B | - | 660 G 4001B POWER MONITORING | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4001B | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 1 | - | 0 | - | 660HS4002D | - | 660 G 4002 LOCAL START | PB | - | - | NORMALLY OPEN | - | - | L | - | BPCS/SIS | MOT | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4002 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 2 | - | 0 | - | 660HSA4002D | - | 660-G-4002 | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4002 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 3 | - | 0 | - | 660HS4002A | - | 660 G 4002 LOCAL ESD | ESD PB | - | - | NORMALLY CLOSE | - | - | L | - | BPCS/SIS | MOT | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4002 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 4 | - | 0 | - | 660HSA4002A | - | 660 G 4002 LOCAL ESD RECOPIE | CONTACT | - | - | NORMALLY CLOSE | - | - | ESS | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4002 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 5 | - | 0 | - | 660HLS4002 | - | 660 G 4002 START/STOP | TPL START/STOP | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4002 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 6 | - | 0 | - | 660HLS4002M | - | 660 G 4002 START | CDE TOR | - | - | NORMALLY OPEN | - | - | ESS | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4002 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 7 | - | 0 | - | 660HLS4002A | - | 660 G 4002 TRIP | CDE TOR | - | - | NORMALLY CLOSE | - | - | ESS | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4002 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 8 | - | 0 | - | 660HLS4002R | - | 660 G 4002 RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4002 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 9 | - | 0 | - | 660XS4002 | - | 660 G 4002 ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1C | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4002 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | S | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 1 | - | 0 | - | 660HS4003D | - | 660 G 4003 LOCAL START | PB | - | - | NORMALLY OPEN | - | - | L | - | BPCS/SIS | MOT | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 2 | - | 0 | - | 660HSA4003D | - | 660-G-4003 | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4003 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 3 | - | 0 | - | 660HS4003A | - | 660 G 4003 LOCAL ESD | ESD PB | - | - | NORMALLY CLOSE | - | - | L | - | BPCS/SIS | MOT | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 4 | - | 0 | - | 660HSA4003A | - | 660 G 4003 LOCAL ESD RECOPIE | CONTACT | - | - | NORMALLY CLOSE | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 5 | - | 0 | - | 660HLS4003 | - | 660 G 4003 START/STOP | TPL START/STOP | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 6 | - | 0 | - | 660HLS4003M | - | 660 G 4003 START | CDE TOR | - | - | NORMALLY OPEN | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 7 | - | 0 | - | 660HLS4003A | - | 660 G 4003 TRIP | CDE TOR | - | - | NORMALLY CLOSE | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 8 | - | 0 | - | 660HLS4003R | - | 660 G 4003 RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 9 | - | 0 | - | 660XS4003 | - | 660 G 4003 ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4003 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 1 | - | 0 | - | 660HS4004D | - | 660 G 4004 LOCAL START | PB | - | - | NORMALLY OPEN | - | - | L | - | BPCS/SIS | MOT | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4004 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 2 | - | 0 | - | 660HSA4004D | - | 660 G 4004 LOCAL START RECOPIE | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4004 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 3 | - | 0 | - | 660HS4004A | - | 660 G 4004 LOCAL ESD | ESD PB | - | - | NORMALLY CLOSE | - | - | L | - | BPCS/SIS | MOT | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4004 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 4 | - | 0 | - | 660HSA4004A | - | 660 G 4004 LOCAL ESD RECOPIE | CONTACT | - | - | NORMALLY CLOSE | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4004 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 5 | - | 0 | - | 660HLS4004 | - | 660 G 4004 START/STOP | TPL STOP | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4004 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 6 | - | 0 | - | 660HLS4004A | - | 660 G 4004 TRIP | CDE TOR | - | - | NORMALLY CLOSE | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4004 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 7 | - | 0 | - | 660HLS4004R | - | 660 G 4004 RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4004 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 8 | - | 0 | - | 660XS4004 | - | 660 G 4004 ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4004 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 11 | - | 0 | - | 660HLS4004M | - | 660 G 4004 START | CDE TOR | - | - | NORMALLY OPEN | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4004 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 1 | - | 0 | - | 660HS4005AD | - | 660 G 4005A LOCAL START | PB | - | - | NORMALLY OPEN | - | - | L | - | BPCS/SIS | MOT | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4005A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 2 | - | 0 | - | 660HSA4005AD | - | 660 G 4005A LOCAL START RECOPIE | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4005A | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 3 | - | 0 | - | 660HS4005AA | - | 660 G 4005A LOCAL ESD | ESD PB | - | - | NORMALLY CLOSE | - | - | L | - | BPCS/SIS | MOT | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4005A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 4 | - | 0 | - | 660HSA4005AA | - | 660 G 4005A LOCAL ESD RECOPIE | CONTACT | - | - | NORMALLY CLOSE | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4005A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 5 | - | 0 | - | 660HLS4005A | - | 660 G 4005A START/STOP | TPL START/STOP | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4005A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 6 | - | 0 | - | 660HLS4005AM | - | 660 G 4005A START | CDE TOR | - | - | NORMALLY OPEN | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4005A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 7 | - | 0 | - | 660HLS4005AA | - | 660 G 4005A TRIP | CDE TOR | - | - | NORMALLY CLOSE | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4005A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 8 | - | 0 | - | 660HLS4005AR | - | 660 G 4005A RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4005A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 9 | - | 0 | - | 660XS4005A | - | 660 G 4005A ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4005A | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 1 | - | 0 | - | 660HS4005BD | - | 660 G 4005B LOCAL START | PB | - | - | NORMALLY OPEN | - | - | L | - | BPCS/SIS | MOT | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4005B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 2 | - | 0 | - | 660HSA4005BD | - | 660 G 4005B LOCAL START RECOPIE | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4005B | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 3 | - | 0 | - | 660HS4005BA | - | 660 G 4005B LOCAL ESD | ESD PB | - | - | NORMALLY CLOSE | - | - | L | - | BPCS/SIS | MOT | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4005B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 4 | - | 0 | - | 660HSA4005BA | - | 660 G 4005B LOCAL ESD RECOPIE | CONTACT | - | - | NORMALLY CLOSE | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4005B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 5 | - | 0 | - | 660HLS4005B | - | 660 G 4005B START/STOP | TPL START/STOP | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4005B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 6 | - | 0 | - | 660HLS4005BM | - | 660 G 4005B START | CDE TOR | - | - | NORMALLY OPEN | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4005B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 7 | - | 0 | - | 660HLS4005BA | - | 660 G 4005B TRIP | CDE TOR | - | - | NORMALLY CLOSE | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4005B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 8 | - | 0 | - | 660HLS4005BR | - | 660 G 4005B RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4005B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 9 | - | 0 | - | 660XS4005B | - | 660 G 4005B ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4005B | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 1 | - | 0 | - | 660HS4006AD | - | 660 G 4006A LOCAL START | PB | - | - | NORMALLY OPEN | - | - | L | - | BPCS/SIS | MOT | - |  |  |  |  | FR-GPS-100-0-OMG-000003 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4006A | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 2 | - | 0 | - | 660HS4006AA | - | 660 G 4006A LOCAL ESD | ESD PB | - | - | NORMALLY CLOSE | - | - | L | - | BPCS/SIS | MOT | - |  |  |  |  | FR-GPS-100-0-OMG-000003 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4006A | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 3 | - | 0 | - | 660HLS4006A | - | 660 G 4006A STOP | TPL STOP | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | FR-GPS-100-0-OMG-000003 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4006A | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 4 | - | 0 | - | 660HLS4006AA | - | 660 G 4006A TRIP | CDE TOR | - | - | NORMALLY CLOSE | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - |  |  |  |  | FR-GPS-100-0-OMG-000003 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4006A | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 5 | - | 0 | - | 660HLS4006AR | - | 660 G 4006A RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - |  |  |  |  | FR-GPS-100-0-OMG-000003 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4006A | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 6 | - | 0 | - | 660XS4006AA | - | 660 G 4006A ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1C | BPCS/SIS | DCS | - |  |  |  |  | FR-GPS-100-0-OMG-000003 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4006A | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | S | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 1 | - | 0 | - | 660HS4006BD | - | 660 G 4006B LOCAL START | PB | - | - | NORMALLY OPEN | - | - | L | - | BPCS/SIS | MOT | - |  |  |  |  | FR-GPS-100-0-OMG-000003 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4006B | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 2 | - | 0 | - | 660HS4006BB | - | 660 G 4006B LOCAL ESD | ESD PB | - | - | NORMALLY CLOSE | - | - | L | - | BPCS/SIS | MOT | - |  |  |  |  | FR-GPS-100-0-OMG-000003 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4006B | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 3 | - | 0 | - | 660HLS4006B | - | 660 G 4006B STOP | TPL STOP | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | FR-GPS-100-0-OMG-000003 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4006B | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 4 | - | 0 | - | 660HLS4006BB | - | 660 G 4006B TRIP | CDE TOR | - | - | NORMALLY CLOSE | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - |  |  |  |  | FR-GPS-100-0-OMG-000003 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4006B | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 5 | - | 0 | - | 660HLS4006BR | - | 660 G 4006B RUNNING STATUS | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1 | BPCS/SIS | S-PLC | - |  |  |  |  | FR-GPS-100-0-OMG-000003 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4006B | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC02 | - | 6 | - | 0 | - | 660XS4006BB | - | 660 G 4006B ELEC FAULT | CONTACT | - | - | NORMALLY OPEN | - | - | ESS | ST1C | BPCS/SIS | DCS | - |  |  |  |  | FR-GPS-100-0-OMG-000003 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660G4006B | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | S | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660HS4010R | - | LPG UNIT ISOLATION AND DEPRESSURIZATION | PB SOFT | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4010 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660HS4010B | - | LPG UNIT ISOLATION AND DEPRESSURIZATION | ESD PB | - | - | - | - | - | L | ST1D | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4010 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS412/P13 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660HS4010A | - | LPG UNIT ISOLATION AND DEPRESSURIZATION | ESD PB | - | - | - | - | - | CRA | ST1D | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4010 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | By OSBL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660XL4010 | - | LPG UNIT ISOLATION AND DEPRESSURIZATION | LIGHT | - | - | - | - | - | L | ST1D | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4010 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJCS414/C11-C12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660HS4011R | - | COMPRESSOR CIRCUIT ISOLATION AND DEPRESSURIZATION | PB SOFT | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4011 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660HS4011B | - | COMPRESSOR CIRCUIT ISOLATION AND DEPRESSURIZATION | ESD PB | - | - | - | - | - | L | ST1D | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4011 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS412/P14 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660HS4011A | - | COMPRESSOR CIRCUIT ISOLATION AND DEPRESSURIZATION | ESD PB | - | - | - | - | - | CRA | ST1D | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4011 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | By OSBL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660XL4011 | - | COMPRESSOR CIRCUIT ISOLATION AND DEPRESSURIZATION | LIGHT | - | - | - | - | - | L | ST1D | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4011 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJCS414/C13-C14 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660HS4012 | - | COMPRESSOR CIRCUIT ISOLATION | PB SOFT | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4012 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660HS4012B | - | COMPRESSOR CIRCUIT ISOLATION | ESD PB | - | - | - | - | - | L | ST1D | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4012 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS412/P15 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660HS4012A | - | COMPRESSOR CIRCUIT ISOLATION | ESD PB | - | - | - | - | - | CRA | ST1D | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4012 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | By OSBL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660XL4012 | - | COMPRESSOR CIRCUIT ISOLATION | LIGHT | - | - | - | - | - | L | ST1D | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4012 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJCS414/C15-C16 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660HS4014A | - | LPG CIRCUIT ISOLATION | ESD PB | - | - | - | - | - | CRA | ST1D | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4014 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | By OSBL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660HS4014B | - | LPG CIRCUIT ISOLATION | ESD PB | - | - | - | - | - | L | ST1D | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4014 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS417/P11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660XL4014 | - | LPG CIRCUIT ISOLATION | LIGHT | - | - | - | - | - | L | ST1D | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4014 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJCS418/C07-C08 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660HS4015R | - | LPG CIRCUIT ISOLATION | PB SOFT | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4015 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660HS4015A | - | LPG CIRCUIT ISOLATION | ESD PB | - | - | - | - | - | CRA | ST1D | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4015 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | By OSBL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660HS4015B | - | LPG CIRCUIT ISOLATION | ESD PB | - | - | - | - | - | L | ST1D | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4015 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS417/P12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660XL4015 | - | LPG CIRCUIT ISOLATION | LIGHT | - | - | - | - | - | L | ST1D | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4015 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJCS418/C09-C10 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660HS4021A | - | LPG PRODUCT PUMPS SHUTDOWN | ESD PB | - | - | - | - | - | CRA | ST1D | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4021 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | By OSBL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660HS4021B | - | LPG PRODUCT PUMPS SHUTDOWN | ESD PB | - | - | - | - | - | L | ST1D | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4021 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS417/P13 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660XL4021 | - | LPG PRODUCT PUMPS SHUTDOWN | LIGHT | - | - | - | - | - | L | ST1D | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4021 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJCS418/C11-C12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660HS4401 | - | 660 K 4001 - LP STOP | PB | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4401 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660LP450 TB2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660XL4401 | - | 660 K 4001 - LP STOP | LIGHT | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4401 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660HS4402 | - | Local Control Panel Compressor | PB | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4402 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660LP450 TB2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660XL4402 | - | Local Control Panel Compressor | LIGHT | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4402 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660HS4403 | - | Local Control Panel Compressor | PB | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4403 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660LP450 TB2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660XL4403 | - | Local Control Panel Compressor | LIGHT | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4403 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660HS4404 | - | Local Control Panel Compressor | PB | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4404 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660LP450 TB2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660XL4404 | - | Local Control Panel Compressor | LIGHT | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4404 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660HS4405 | - | Local Control Panel Compressor | PB | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4405 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660LP450 TB2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660XL4405 | - | Local Control Panel Compressor | LIGHT | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4405 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | 660LP450 TB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660HS4406 | - | Local Control Panel Compressor | PB | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4406 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660LP450 TB2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660XL4406 | - | Local Control Panel Compressor | LIGHT | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4406 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | 660LP450 TB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660HS4411 | - | 660 K 4001 - LP LOCAL/REMOTE | PB | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4411 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660LP450 TB2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660HS4411B | - | 660 K 4001 - LP REMOTE (SIGNAL) | PB | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4411 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660LP450 TB2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660HS4412 | - | 660 K 4001 - EMERGENCY STOP | PB | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4412 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660LP450 TB2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660HS4412B | - | 660 K 4001 - EMERGENCY STOP (SIGNAL) | PB | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4412 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660LP450 TB2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660HS4413 | - | EMERGENCY STOP - PB ON COMPRESSOR SKID | PB | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4413 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660LP450 TB2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660HS4500 | - | 660-K-4001 SECOND STAGE | ESD PB | - | - | NORMALLY CLOSE | - | - | CRA | ST1D | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0402 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4500 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | By OSBL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660HLS4501 | - | 660-K-4001 SECOND STAGE | TPL STOP | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0402 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660H4500 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 1 | - | 0 | - | 660HSK4001D | - | 660 KM 4001 LOCAL START | PB | - | - | - | - | - | L | - | SIS | MOT | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660K4001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 2 | - | 0 | - | 660HSAK4001D | - | 660 KM 4001 RECOPIE LOCAL START | CONTACT | - | - | - | - | - | ESS | P11 | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660K4001 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 3 | - | 0 | - | 660HSK4001A | - | 660 KM 4001 LOCAL ESD | ESD PB | - | - | - | - | - | L | - | SIS | MOT | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660K4001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | E | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 4 | - | 0 | - | 660HSAK4001A | - | 660 KM 4001 LOCAL ESD RECOPIE | CONTACT | - | - | - | - | - | ESS | P11 | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660K4001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 5 | - | 0 | - | 660HLSK4001 | - | 660 KM 4001 START/STOP | TPL STOP | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660K4001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 6 | - | 0 | - | 660HLSK4001A | - | 660 KM 4001 TRIP | CDE TOR | - | - | - | - | - | ESS | P11 | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660K4001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 7 | - | 0 | - | 660HLSK4001R | - | 660 KM 4001 RUNNING STATUS | CONTACT | - | - | - | - | - | ESS | P11 | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660K4001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 8 | - | 0 | - | 660XSK4001 | - | 660 KM 4001 ELEC FAULT | CONTACT | - | - | - | - | - | ESS | P11 | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660K4001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | MCC04 | - | 11 | - | 0 | - | 660HLSK4001M | - | 660 KM 4001 START | CDE TOR | - | - | - | - | - | ESS | P11 | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660K4001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660LTS4020A | - | 660-D-4001 | PRESSURE DP | - | - | W/T SEAL+CAPILLARY | - | - | L | ST1D | BPCS/SIS | S-PLC | - | 0 | 1000 |  | mm | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4020 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS451/P01 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660LTS4020B | - | 660-D-4001 | PRESSURE DP | - | - | W/T SEAL+CAPILLARY | - | - | L | ST1D | BPCS/SIS | S-PLC | - | 0 | 1000 |  | mm | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4020 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS452/P01 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660LTS4020C | - | 660-D-4001 | PRESSURE DP | - | - | W/T SEAL+CAPILLARY | - | - | L | ST1D | BPCS/SIS | S-PLC | - | 0 | 1000 |  | mm | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4020 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS453/P01 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660LI4020A | - | 660-D-4001 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4020 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660LI4020B | - | 660-D-4001 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4020 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 0 | - | 660LI4020C | - | 660-D-4001 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4020 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 0 | - | 660LSHH4020A | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 900 | mm | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4020 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 0 | - | 660LSLL4020A | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 300 | mm | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4020 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 9 | - | 0 | - | 660LSHH4020B | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 900 | mm | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4020 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 10 | - | 0 | - | 660LSLL4020B | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 300 | mm | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4020 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 11 | - | 0 | - | 660LSHH4020C | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 900 | mm | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4020 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 12 | - | 0 | - | 660LSLL4020C | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 300 | mm | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4020 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 13 | - | 0 | - | 660LAH4020 | - | 660-D-4001 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  | 750 | mm | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4020 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 14 | - | 0 | - | 660LAL4020 | - | 660-D-4001 | LOW LEVEL ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  | 450 | mm | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4020 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660LTS4023A | - | 660-D-4002 | PRESSURE DP | - | - | W/T SEAL+CAPILLARY | - | - | L | ST1D | BPCS/SIS | CONV | - | 0 | 1000 |  | mm | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4023 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660BJMS451/P02 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660LTS4023B | - | 660-D-4002 | PRESSURE DP | - | - | W/T SEAL+CAPILLARY | - | - | L | ST1D | BPCS/SIS | CONV | - | 0 | 1000 |  | mm | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4023 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660BJMS452/P02 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660LTS4023C | - | 660-D-4002 | PRESSURE DP | - | - | W/T SEAL+CAPILLARY | - | - | L | ST1D | BPCS/SIS | CONV | - | 0 | 1000 |  | mm | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4023 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660BJMS453/P02 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660LTS4023AA | - | 660-D-4002 | OUTPUT CONVERTER | - | - | I/I | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4023 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660LTS4023BA | - | 660-D-4002 | OUTPUT CONVERTER | - | - | I/I | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4023 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 0 | - | 660LTS4023CA | - | 660-D-4002 | OUTPUT CONVERTER | - | - | I/I | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4023 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 0 | - | 660LTS4023AB | - | 660-D-4002 | OUTPUT CONVERTER | - | - | I/I | - | - | ITR | ST1C | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4023 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | EXT | - | - | - | S | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 0 | - | 660LTS4023BB | - | 660-D-4002 | OUTPUT CONVERTER | - | - | I/I | - | - | ITR | ST1C | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4023 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | EXT | - | - | - | S | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 9 | - | 0 | - | 660LTS4023CB | - | 660-D-4002 | OUTPUT CONVERTER | - | - | I/I | - | - | ITR | ST1C | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4023 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | EXT | - | - | - | S | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 10 | - | 0 | - | 660LI4023A | - | 660-D-4002 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4023 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 11 | - | 0 | - | 660LI4023B | - | 660-D-4002 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4023 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 12 | - | 0 | - | 660LI4023C | - | 660-D-4002 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4023 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 13 | - | 0 | - | 660LSHH4023A | - | 660-D-4002 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 900 | mm | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4023 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 14 | - | 0 | - | 660LSHH4023B | - | 660-D-4002 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 900 | mm | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4023 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 15 | - | 0 | - | 660LSHH4023C | - | 660-D-4002 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 900 | mm | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4023 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 16 | - | 0 | - | 660LAH4023 | - | 660-D-4002 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | 750 | mm | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4023 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 18 | - | 0 | - | 660LSLL4023A | - | 660-D-4002 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 300 | mm | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4023 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 19 | - | 0 | - | 660LSLL4023B | - | 660-D-4002 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 300 | mm | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4023 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 20 | - | 0 | - | 660LSLL4023C | - | 660-D-4002 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 300 | mm | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4023 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 21 | - | 0 | - | 660LAL4023 | - | 660-D-4002 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | 450 | mm | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4023 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 22 | - | 0 | - | 660LC4023 | - | 660-D-4002 | CONTROLLER | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0404 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4023 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | CV01 | - | 23 | - | 0 | - | 660LV4023A | - | LPG from second stage KO Drum | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0404 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4023 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJM406/P01 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | CV01 | - | 24 | - | 0 | - | 660LV4023B | - | LPG from second stage KO Drum | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0404 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4023 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJM406/P02 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 25 | - | 0 | - | 660LY4023A | - | 660-D-4002 | SOFT CALCULATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0404 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4023 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 26 | - | 0 | - | 660LY4023B | - | 660-D-4002 | SOFT CALCULATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0404 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4023 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660LAH4025 | - | 660-D-4002 | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0404 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4025 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660LAL4025 | - | 660-D-4002 | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0404 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4025 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660LC4025 | - | 660-D-4002 | CONTROLLER | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0404 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4025 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660LT4025 | - | 660-D-4002 | PRESSURE DP | - | - | W/T SEAL+CAPILLARY | - | - | L | ST1C | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0404 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4025 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660LTS4026A | - | 660-D-4003 | PRESSURE DP | - | - | W/T SEAL+CAPILLARY | - | - | L | ST1D | BPCS/SIS | CONV | - | 0 | 100 |  | % | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4026 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660BJMS407/P01 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660LTS4026B | - | 660-D-4003 | PRESSURE DP | - | - | W/T SEAL+CAPILLARY | - | - | L | ST1D | BPCS/SIS | CONV | - | 0 | 100 |  | % | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4026 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660BJMS407/P02 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660LTS4026C | - | 660-D-4003 | PRESSURE DP | - | - | W/T SEAL+CAPILLARY | - | - | L | ST1D | BPCS/SIS | CONV | - | 0 | 100 |  | % | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4026 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660BJMS404/P01 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660LTS4026AA | - | 660-D-4003 | OUTPUT CONVERTER | - | - | I/I | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4026 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660LTS4026BA | - | 660-D-4003 | OUTPUT CONVERTER | - | - | I/I | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4026 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 0 | - | 660LTS4026CA | - | 660-D-4003 | OUTPUT CONVERTER | - | - | I/I | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4026 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 0 | - | 660LTS4026AB | - | 660-D-4003 | OUTPUT CONVERTER | - | - | I/I | - | - | ITR | ST1C | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4026 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | EXT | - | - | - | S | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 0 | - | 660LTS4026BB | - | 660-D-4003 | OUTPUT CONVERTER | - | - | I/I | - | - | ITR | ST1C | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4026 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | EXT | - | - | - | S | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 9 | - | 0 | - | 660LTS4026CB | - | 660-D-4003 | OUTPUT CONVERTER | - | - | I/I | - | - | ITR | ST1C | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4026 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | EXT | - | - | - | S | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 10 | - | 0 | - | 660LI4026A | - | 60-D-4003 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4026 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 11 | - | 0 | - | 660LI4026B | - | 60-D-4003 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4026 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 12 | - | 0 | - | 660LI4026C | - | 60-D-4003 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4026 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 13 | - | 0 | - | 660LSHH4026A | - | 60-D-4003 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 2100 mm(88.37%) |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4026 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 14 | - | 0 | - | 660LSHH4026B | - | 60-D-4003 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 2100 mm(88.37%) |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4026 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 15 | - | 0 | - | 660LSHH4026C | - | 60-D-4003 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 2100 mm(88.37%) |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4026 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 16 | - | 0 | - | 660LAH4026 | - | 60-D-4003 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | 1700 mm(69.77%) |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4026 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 18 | - | 0 | - | 660LSLL4026A | - | 60-D-4003 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 300 mm(4.65%) |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4026 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 19 | - | 0 | - | 660LSLL4026B | - | 60-D-4003 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 300 mm(4.65%) |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4026 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 20 | - | 0 | - | 660LSLL4026C | - | 60-D-4003 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 300 mm(4.65%) |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4026 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 21 | - | 0 | - | 660LAL4026 | - | 60-D-4003 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | 700 mm(23.26%) |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4026 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 22 | - | 0 | - | 660LC4026 | - | 60-D-4003 | CONTROLLER | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4026 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | CV04 | - | 23 | - | 0 | - | 660LV4026A | - | LPG from HP LPG Separator | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4026 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJM406/P03 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | CV04 | - | 24 | - | 0 | - | 660LV4026B | - | LPG from HP LPG Separator | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4026 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJM406/P04 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 25 | - | 0 | - | 660UYS4026A | - | LPG from HP LPG Separator | AIR SOLENOID SPRING | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4026 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJCS418/C15-C16 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 26 | - | 0 | - | 660UYS4026B | - | LPG from HP LPG Separator | AIR SOLENOID SPRING | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4026 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJCS418/C17-C18 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 27 | - | 0 | - | 660LZSL4026A | - | LPG from HP LPG Separator | LIMIT SWITCH | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4026 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS417/P09 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 28 | - | 0 | - | 660LZSL4026B | - | LPG from HP LPG Separator | LIMIT SWITCH | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4026 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS417/P10 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 31 | - | 0 | - | 660LY4026A | - | 60-D-4003 | SOFT CALCULATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4026 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 32 | - | 0 | - | 660LY4026B | - | 60-D-4003 | SOFT CALCULATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4026 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660LAH4028 | - | 60-D-4003 | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4028 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660LAL4028 | - | 60-D-4003 | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4028 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660LC4028 | - | 60-D-4003 | CONTROLLER | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4028 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660LT4028 | - | 60-D-4003 | PRESSURE DP | - | - | W/T SEAL+CAPILLARY | - | - | L | ST1C | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4028 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660LAH4029 | - | FROM 660-D-4004 | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4029 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660LAL4029 | - | FROM 660-D-4004 | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4029 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660LC4029 | - | FROM 660-D-4004 | CONTROLLER | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4029 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660LDT4029 | - | FROM 660-D-4004 | GUIDED WAVE RADAR | - | - | 2 WIRES | - | - | L | ST1C | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4029 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660LAH4032 | - | 660-D-4004 | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4032 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660LAL4032 | - | 660-D-4004 | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4032 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660LC4032 | - | 660-D-4004 | CONTROLLER | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4032 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660LT4032 | - | 660-D-4004 | PRESSURE DP | - | - | W/T SEAL+CAPILLARY | - | - | L | ST1C | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4032 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660LY4032 | - | 660-D-4004 | SOFT CALCULATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4032 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660LTS4033A | - | 660-D-4004 | PRESSURE DP | - | - | W/T SEAL+CAPILLARY | - | - | L | ST1D | BPCS/SIS | CONV | - | 0 | 100 |  | % | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4033 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660BJMS408/P01 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660LTS4033B | - | 660-D-4004 | PRESSURE DP | - | - | W/T SEAL+CAPILLARY | - | - | L | ST1D | BPCS/SIS | CONV | - | 0 | 100 |  | % | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4033 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660BJMS408/P02 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660LTS4033C | - | 660-D-4004 | PRESSURE DP | - | - | W/T SEAL+CAPILLARY | - | - | L | ST1D | BPCS/SIS | CONV | - | 0 | 100 |  | % | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4033 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660BJMS405/P01 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660LTS4033AA | - | 660-D-4004 | OUTPUT CONVERTER | - | - | I/I | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4033 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660LTS4033BA | - | 660-D-4004 | OUTPUT CONVERTER | - | - | I/I | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4033 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 0 | - | 660LTS4033CA | - | 660-D-4004 | OUTPUT CONVERTER | - | - | I/I | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4033 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 0 | - | 660LTS4033AB | - | 660-D-4004 | OUTPUT CONVERTER | - | - | I/I | - | - | ITR | ST1C | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4033 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | EXT | - | - | - | S | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 0 | - | 660LTS4033BB | - | 660-D-4004 | OUTPUT CONVERTER | - | - | I/I | - | - | ITR | ST1C | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4033 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | EXT | - | - | - | S | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 9 | - | 0 | - | 660LTS4033CB | - | 660-D-4004 | OUTPUT CONVERTER | - | - | I/I | - | - | ITR | ST1C | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4033 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | EXT | - | - | - | S | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 10 | - | 0 | - | 660LI4033A | - | 660-D-4004 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4033 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 11 | - | 0 | - | 660LI4033B | - | 660-D-4004 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4033 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 12 | - | 0 | - | 660LI4033C | - | 660-D-4004 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4033 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 13 | - | 0 | - | 660LSHH4033A | - | 660-D-4004 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 900 mm (87.50%) |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4033 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 14 | - | 0 | - | 660LSHH4033B | - | 660-D-4004 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 900 mm (87.50%) |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4033 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 15 | - | 0 | - | 660LSHH4033C | - | 660-D-4004 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 900 mm (87.50%) |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4033 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 16 | - | 0 | - | 660LAH4033 | - | 660-D-4004 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | 750 mm (68.75%) |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4033 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 18 | - | 0 | - | 660LSLL4033A | - | 660-D-4004 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 300 mm (4.65%) |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4033 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 19 | - | 0 | - | 660LSLL4033B | - | 660-D-4004 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 300 mm (4.65%) |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4033 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 20 | - | 0 | - | 660LSLL4033C | - | 660-D-4004 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 300 mm (4.65%) |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4033 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 21 | - | 0 | - | 660LAL4033 | - | 660-D-4004 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | 450 mm (31.25%) |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4033 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 22 | - | 0 | - | 660LC4033 | - | 660-D-4004 | CONTROLLER | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4033 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660LDT4034 | - | 660-D-4004 | PRESSURE DP | - | - | W/T SEAL+CAPILLARY | - | - | L | ST1C | BPCS/SIS | DCS | - | 0 | 100 |  | % | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4034 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM401/P14 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660LDTS4034C | - | 660-D-4004 | PRESSURE DP | - | - | W/T SEAL+CAPILLARY | - | - | L | ST1D | BPCS/SIS | CONV | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4034 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660LDTS4034AA | - | 660-D-4004 | OUTPUT CONVERTER | - | - | I/I | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4034 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660LDTS4034BA | - | 660-D-4004 | OUTPUT CONVERTER | - | - | I/I | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4034 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 0 | - | 660LDTS4034CA | - | 660-D-4004 | OUTPUT CONVERTER | - | - | I/I | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4034 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 0 | - | 660LDTS4034AB | - | 660-D-4004 | OUTPUT CONVERTER | - | - | I/I | - | - | ITR | ST1C | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4034 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | EXT | - | - | - | S | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 0 | - | 660LDTS4034BB | - | 660-D-4004 | OUTPUT CONVERTER | - | - | I/I | - | - | ITR | ST1C | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4034 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | EXT | - | - | - | S | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 9 | - | 0 | - | 660LDTS4034CB | - | 660-D-4004 | OUTPUT CONVERTER | - | - | I/I | - | - | ITR | ST1C | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4034 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | EXT | - | - | - | S | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 10 | - | 0 | - | 660LI4034A | - | 660-D-4004 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4034 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 11 | - | 0 | - | 660LI4034B | - | 660-D-4004 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4034 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 12 | - | 0 | - | 660LI4034C | - | 660-D-4004 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4034 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 13 | - | 0 | - | 660LSHH4034A | - | 660-D-4004 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4034 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 14 | - | 0 | - | 660LSHH4034B | - | 660-D-4004 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4034 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 15 | - | 0 | - | 660LSHH4034C | - | 660-D-4004 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4034 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 16 | - | 0 | - | 660LAH4034 | - | 660-D-4004 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4034 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 18 | - | 0 | - | 660LSLL4034A | - | 660-D-4004 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4034 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 19 | - | 0 | - | 660LSLL4034B | - | 660-D-4004 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4034 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 20 | - | 0 | - | 660LSLL4034C | - | 660-D-4004 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4034 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 21 | - | 0 | - | 660LAL4034 | - | 660-D-4004 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4034 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 22 | - | 0 | - | 660LC4034 | - | 660-D-4004 | CONTROLLER | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4034 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | CV01 | - | 23 | - | 0 | - | 660LDV4034 | - | LP LPG Separator Water Product to SWS | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4034 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJM401/P03 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 24 | - | 0 | - | 660LDI4034 | - | 660-D-4004 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4034 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 25 | - | 0 | - | 660LDC4034 | - | 660-D-4004 | CONTROLLER | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4034 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 26 | - | 0 | - | 660LDAH4034 | - | 660-D-4004 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | 750 mm (64.70%) |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4034 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 27 | - | 0 | - | 660LDAL4034 | - | 660-D-4004 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | 450 mm (29.41%) |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4034 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660LT4035 | - | 660 D 4006 | PRESSURE DP | - | - | W/T SEAL | - | - | L | ST1C | BPCS | DCS | - | 0 | 100 |  | % | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4035 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM409/P01 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660LI4035 | - | 660 D 4006 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4035 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660LAH4035 | - | 660 D 4006 | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 570 mm (74%) |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4035 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660LDT4037 | - | 660-D-4005 | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 100 |  | % | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4037 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJM409/P02 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660LDI4037 | - | 660-D-4005 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4037 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660LC4037 | - | 660-D-4005 | CONTROLLER | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4037 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660LSL4037 | - | 660-D-4005 | SOFT THERSHOLD | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 450 mm (41.67%) |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4037 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660LSH4037 | - | 660-D-4005 | SOFT THERSHOLD | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 700 mm (83.33%) |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4037 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | CV01 | - | 6 | - | 0 | - | 660LDV4037 | - | Brine to 660-D-4006 | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4037 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJM409/P03 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660LDTS4039 | - | 660 D 4005 | PRESSURE DP | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | 0 | 100 |  | % | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4039 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS410/P01 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660LDI4039 | - | 660 D 4005 | INDICATION | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4039 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660LSLL4039 | - | 660 D 4005 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | SIS | S-PLC | - |  |  | 300 mm (16.67%) |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4039 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660LDTS4052 | - | 660D4004 | PRESSURE DP | - | - | W/T SEAL+CAPILLARY | - | - | L | ST1D | SIS | S-PLC | - | 0 | 100 |  | % | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4052 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS408/P05 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660LDI4052 | - | 660D4004 | INDICATION | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4052 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660LDSLL4052 | - | 660D4004 | SOFT THERSHOLD | - | - | - | - | - | ITR | ST1D | SIS | S-PLC | - |  |  | 300 mm (11.76%) |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4052 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660LS4338 | - | 660G4001A | LEVEL SWITCH | - | - | - | - | - | L | ST1D | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4338 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS405/P02 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660LSH4338 | - | 660G4001A | SOFT THERSHOLD | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4338 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660LS4343 | - | 660G4001B | LEVEL SWITCH | - | - | - | - | - | L | ST1D | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4343 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS405/P03 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660LSH4343 | - | 660G4001B | SOFT THERSHOLD | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4343 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660LT4450 | - | METHANOL INJECTION PUMPS 660G4006A | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 375 | 1450 |  | mm | FR-GPS-100-0-OMG-000003 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4450 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 662BJM130/P20 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660LI4450 | - | METHANOL INJECTION PUMPS 660G4006A | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | FR-GPS-100-0-OMG-000003 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4450 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660LAL4450 | - | METHANOL INJECTION PUMPS 660G4006A | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 375 | mm | FR-GPS-100-0-OMG-000003 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4450 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660LS4500A | - | 660-D-4009 | LEVEL SWITCH | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | 8 | 16 |  | mA | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4500 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS451/P13 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660LS4500B | - | 660-D-4009 | LEVEL SWITCH | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | 8 | 16 |  | mA | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4500 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS452/P13 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660LS4502 | - | 660-E-4006 | LEVEL SWITCH | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | 8 | 16 |  | mA | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4502 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS451/P14 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660LTS4504 | - | 660-D-4010 | PRESSURE DP | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | 0 | 600 |  | mm | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4504 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS452/P03 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660LI4504 | - | 660-D-4010 | INDICATION | - | - | - | - | - | CRD | ST1D | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4504 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660LSLL4504 | - | 660-D-4010 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | SIS | S-PLC | - |  |  | 200 | mm | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4504 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660LT4506 | - | Leakage Gas Distance Piece 2nd Stage | LEVEL TRANSMITTER | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 300 |  | mm | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4506 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM454/P01 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660LI4506 | - | Leakage Gas Distance Piece 2nd Stage | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660L4506 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660PTS4221 | - | HDT PURGE FROM 662C3001 | PRESSURE REL | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | 0 | 60 |  | bar | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4221 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS405/P04 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660PI4221 | - | HDT PURGE FROM 662C3001 | INDICATION | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4221 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660PSHH4221 | - | HDT PURGE FROM 662C3001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | SIS | S-PLC | - |  |  | 43 | bar | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4221 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660PT4238 | - | STEAM TO 660-E-4004 | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 10 |  | bar | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4238 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM401/P15 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660PI4238 | - | STEAM TO 660-E-4004 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4238 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660PTS4320A | - | 660-D-4001 | PRESSURE REL | - | - | - | - | - | L | ST1D | BPCS/SIS | CONV | - | -1 | 15 |  | bar | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4320 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660BJMS451/P05 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660PTS4320B | - | 660-D-4001 | PRESSURE REL | - | - | - | - | - | L | ST1D | BPCS/SIS | CONV | - | -1 | 15 |  | bar | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4320 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660BJMS452/P06 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660PTS4320C | - | 660-D-4001 | PRESSURE REL | - | - | - | - | - | L | ST1D | BPCS/SIS | CONV | - | -1 | 15 |  | bar | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4320 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 660BJMS453/P05 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660PTS4320AA | - | 660-D-4001 | OUTPUT CONVERTER | - | - | I/I | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4320 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660PTS4320BA | - | 660-D-4001 | OUTPUT CONVERTER | - | - | I/I | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4320 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 0 | - | 660PTS4320CA | - | 660-D-4001 | OUTPUT CONVERTER | - | - | I/I | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4320 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 0 | - | 660PTS4320AB | - | 660-D-4001 | OUTPUT CONVERTER | - | - | I/I | - | - | ITR | ST1C | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4320 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | EXT | - | - | - | S | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 0 | - | 660PTS4320BB | - | 660-D-4001 | OUTPUT CONVERTER | - | - | I/I | - | - | ITR | ST1C | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4320 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | EXT | - | - | - | S | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 9 | - | 0 | - | 660PTS4320CB | - | 660-D-4001 | OUTPUT CONVERTER | - | - | I/I | - | - | ITR | ST1C | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4320 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | EXT | - | - | - | S | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 10 | - | 0 | - | 660PI4320A | - | 660-D-4001 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4320 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 11 | - | 0 | - | 660PI4320B | - | 660-D-4001 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4320 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 12 | - | 0 | - | 660PI4320C | - | 660-D-4001 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4320 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 13 | - | 0 | - | 660PSHH4320A | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 4.1 | bar | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4320 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 14 | - | 0 | - | 660PSHH4320B | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 4.1 | bar | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4320 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 15 | - | 0 | - | 660PSHH4320C | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 4.1 | bar | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4320 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 16 | - | 0 | - | 660PAH4320 | - | 660-D-4001 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | 3.7 | bar | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4320 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 18 | - | 0 | - | 660PSLL4320A | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 2.1 | bar | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4320 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 19 | - | 0 | - | 660PSLL4320B | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 2.1 | bar | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4320 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 20 | - | 0 | - | 660PSLL4320C | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 2.1 | bar | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4320 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 21 | - | 0 | - | 660PAL4320 | - | 660-D-4001 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | 2.5 | bar | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4320 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 22 | - | 0 | - | 660PC4320 | - | 660-D-4001 | CONTROLLER | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4320 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | CV01 | - | 23 | - | 0 | - | 660PV4320A | - | Spillback 1st stage | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4320 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJM406/P05 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | CV01 | - | 24 | - | 0 | - | 660PV4320B | - | Off Gas to Flare header from 660-D-4001 | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4320 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJM406/P06 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 25 | - | 0 | - | 660PY4320A | - | 660-D-4001 | SOFT CALCULATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4320 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 26 | - | 0 | - | 660PY4320B | - | 660-D-4001 | SOFT CALCULATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4320 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660PTS4325A | - | WET GAS FROM 660-D-4002 | PRESSURE REL | - | - | - | - | - | L | ST1D | SIS | CONV | - | -1 | 15 |  | bar | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4325 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | R | - | - | - | - | - | - | 660BJMS451/P03 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660PI4325A | - | WET GAS FROM 660-D-4002 | INDICATION | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4325 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660PC4325 | - | WET GAS FROM 660-D-4002 | CONTROLLER | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4325 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660PAL4325 | - | WET GAS FROM 660-D-4002 | ALARM | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  | 10.7 | bar | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4325 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660PAH4325 | - | WET GAS FROM 660-D-4002 | ALARM | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  | 13.2 | bar | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4325 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | CV01 | - | 6 | - | 0 | - | 660PV4325A | - | Spillback 2nd stage | CONTROL VALVE | - | - | - | - | - | L | ST1C | SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0404 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4325 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJM406/P07 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | CV01 | - | 7 | - | 0 | - | 660PV4325B | - | Off Gas to flare Header from 660-D-4002 | CONTROL VALVE | - | - | - | - | - | L | ST1C | SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0404 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4325 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJM406/P08 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 0 | - | 660PY4325A | - | WET GAS FROM 660-D-4002 | SOFT CALCULATION | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4325 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 9 | - | 0 | - | 660PY4325B | - | WET GAS FROM 660-D-4002 | SOFT CALCULATION | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4325 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 10 | - | 0 | - | 660PTS4325B | - | WET GAS FROM 660-D-4002 | PRESSURE REL | - | - | - | - | - | L | ST1D | SIS | CONV | - | -1 | 15 |  | bar | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4325 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | R | - | - | - | - | - | - | 660BJMS452/P04 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 11 | - | 0 | - | 660PTS4325C | - | WET GAS FROM 660-D-4002 | PRESSURE REL | - | - | - | - | - | L | ST1D | SIS | CONV | - | -1 | 15 |  | bar | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4325 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | R | - | - | - | - | - | - | 660BJMS453/P03 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 12 | - | 0 | - | 660PSLL4325A | - | WET GAS FROM 660-D-4002 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | SIS | S-PLC | - |  |  | 10.2 | bar | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4325 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 13 | - | 0 | - | 660PTS4325AA | - | WET GAS FROM 660-D-4002 | OUTPUT CONVERTER | - | - | - | - | - | ITR | ST1D | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4325 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 14 | - | 0 | - | 660PTS4325BA | - | WET GAS FROM 660-D-4002 | OUTPUT CONVERTER | - | - | - | - | - | ITR | ST1D | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4325 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 15 | - | 0 | - | 660PTS4325CA | - | WET GAS FROM 660-D-4002 | OUTPUT CONVERTER | - | - | - | - | - | ITR | ST1D | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4325 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 16 | - | 0 | - | 660PTS4325AB | - | WET GAS FROM 660-D-4002 | OUTPUT CONVERTER | - | - | - | - | - | ITR | ST1C | SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4325 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | EXT | - | - | - | S | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 17 | - | 0 | - | 660PTS4325BB | - | WET GAS FROM 660-D-4002 | OUTPUT CONVERTER | - | - | - | - | - | ITR | ST1C | SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4325 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | EXT | - | - | - | S | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 18 | - | 0 | - | 660PTS4325CB | - | WET GAS FROM 660-D-4002 | OUTPUT CONVERTER | - | - | - | - | - | ITR | ST1C | SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4325 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | EXT | - | - | - | S | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 19 | - | 0 | - | 660PSLL4325B | - | WET GAS FROM 660-D-4002 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | SIS | S-PLC | - |  |  | 10.2 | bar | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4325 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 20 | - | 0 | - | 660PSLL4325C | - | WET GAS FROM 660-D-4002 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | SIS | S-PLC | - |  |  | 10.2 | bar | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4325 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 21 | - | 0 | - | 660PSHH4325B | - | WET GAS FROM 660-D-4002 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | SIS | S-PLC | - |  |  | 13.7 | bar | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4325 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 22 | - | 0 | - | 660PSHH4325C | - | WET GAS FROM 660-D-4002 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | SIS | S-PLC | - |  |  | 13.7 | bar | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4325 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 23 | - | 0 | - | 660PSHH4325A | - | WET GAS FROM 660-D-4002 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | SIS | S-PLC | - |  |  | 13.7 | bar | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4325 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 24 | - | 0 | - | 660PI4325B | - | WET GAS FROM 660-D-4002 | INDICATION | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4325 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 25 | - | 0 | - | 660PI4325C | - | WET GAS FROM 660-D-4002 | INDICATION | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4325 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660PT4327 | - | Wet Gas From 660-D-4003 To SMR | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 60 |  | bar | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4327 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJM403/P02 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660PI4327 | - | Wet Gas From 660-D-4003 To SMR | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4327 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660PC4327 | - | Wet Gas From 660-D-4003 To SMR | CONTROLLER | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4327 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | CV01 | - | 4 | - | 0 | - | 660PV4327A | - | OFF GAS TO FLARE | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4327 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJM403/P03 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | CV01 | - | 5 | - | 0 | - | 660PV4327B | - | OFF GAS TO SMR | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4327 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJM403/P04 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 0 | - | 660PY4327A | - | Wet Gas From 660-D-4003 To SMR | SOFT CALCULATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4327 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 0 | - | 660PY4327B | - | Wet Gas From 660-D-4003 To SMR | SOFT CALCULATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4327 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660PT4329 | - | Off Gas From 660-D-4004 To 660-D-4001 | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 10 |  | bar | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4329 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJM401/P04 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660PI4329 | - | Off Gas From 660-D-4004 To 660-D-4001 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4329 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660PC4329 | - | Off Gas From 660-D-4004 To 660-D-4001 | CONTROLLER | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4329 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | CV01 | - | 4 | - | 0 | - | 660PV4329A | - | Recycle off-gas from 660-D-4004 | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4329 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJM401/P05 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | CV01 | - | 5 | - | 0 | - | 660PV4329B | - | Recycle off-gas from 660-D-4004 | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4329 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJM401/P06 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 0 | - | 660PAH4329 | - | Off Gas From 660-D-4004 To 660-D-4001 | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 6 | bar | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4329 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 0 | - | 660PY4329A | - | Off Gas From 660-D-4004 To 660-D-4001 | SOFT CALCULATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4329 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 0 | - | 660PY4329B | - | Off Gas From 660-D-4004 To 660-D-4001 | SOFT CALCULATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4329 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660PTS4332A | - | 660-D-4001 | PRESSURE REL | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4332 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660PTS4332B | - | 660-D-4001 | PRESSURE REL | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4332 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660PTS4332C | - | 660-D-4001 | PRESSURE REL | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4332 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660PI4332A | - | 660-D-4001 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4332 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660PI4332B | - | 660-D-4001 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4332 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 0 | - | 660PI4332C | - | 660-D-4001 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4332 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 0 | - | 660PSHH4332A | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | hold |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4332 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 0 | - | 660PSLL4332A | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | hold |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4332 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 9 | - | 0 | - | 660PSHH4332B | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | hold |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4332 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 10 | - | 0 | - | 660PSLL4332B | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | hold |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4332 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 11 | - | 0 | - | 660PSHH4332C | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | hold |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4332 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 12 | - | 0 | - | 660PSLL4332C | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | hold |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4332 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 14 | - | 0 | - | 660PAL4332 | - | 660-D-4001 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4332 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 15 | - | 0 | - | 660PAH4332 | - | 660-D-4001 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4332 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660PTS4333A | - | 660-D-4001 | PRESSURE REL | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | -1 | 50 |  | bar | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4333 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS451/P04 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660PTS4333B | - | 660-D-4001 | PRESSURE REL | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | -1 | 50 |  | bar | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4333 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS452/P05 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660PTS4333C | - | 660-D-4001 | PRESSURE REL | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | -1 | 50 |  | bar | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4333 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS453/P04 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660PI4333A | - | 660-D-4001 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4333 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660PI4333B | - | 660-D-4001 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4333 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 0 | - | 660PI4333C | - | 660-D-4001 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4333 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 0 | - | 660PSHH4333A | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 44.5 | bar | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4333 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 0 | - | 660PSHH4333B | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 44.5 | bar | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4333 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 9 | - | 0 | - | 660PSHH4333C | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 44.5 | bar | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4333 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 10 | - | 0 | - | 660PAH4333 | - | 660-D-4001 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | 43.5 | bar | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4333 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660PTS4334 | - | 660-G-4001A Suction | PRESSURE REL | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | 0 | 10 |  | bar | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4334 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS408/P07 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660PI4334 | - | 660-G-4001A Suction | INDICATION | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4334 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660PSLL4334 | - | 660-G-4001A Suction | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | SIS | S-PLC | - |  |  | 5.5 | bar | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4334 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660PTS4335 | - | Off Gas From 660-D-4004 To 660-D-4001 | PRESSURE REL | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | 0 | 10 |  | bar | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4335 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS408/P03 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660PI4335 | - | Off Gas From 660-D-4004 To 660-D-4001 | INDICATION | - | - | - | - | - | CRD | ST1D | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4335 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660PSHH4335 | - | Off Gas From 660-D-4004 To 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | SIS | S-PLC | - |  |  | 6.5 | bar | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4335 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660PTS4336A | - | 660-D-4001 | PRESSURE REL | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4336 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660PTS4336B | - | 660-D-4001 | PRESSURE REL | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4336 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660PTS4336C | - | 660-D-4001 | PRESSURE REL | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4336 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660PI4336A | - | 660-D-4001 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4336 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660PI4336B | - | 660-D-4001 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4336 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 0 | - | 660PI4336C | - | 660-D-4001 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4336 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 0 | - | 660PSHH4336A | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | hold |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4336 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 0 | - | 660PSLL4336A | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | hold |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4336 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 9 | - | 0 | - | 660PSHH4336B | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | hold |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4336 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 10 | - | 0 | - | 660PSLL4336B | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | hold |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4336 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 11 | - | 0 | - | 660PSHH4336C | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | hold |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4336 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 12 | - | 0 | - | 660PSLL4336C | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | hold |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4336 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660PTS4337A | - | 660-D-4001 | PRESSURE REL | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | -1 | 15 |  | bar | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4337 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS451/P06 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660PTS4337B | - | 660-D-4001 | PRESSURE REL | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | -1 | 15 |  | bar | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4337 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS452/P07 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660PTS4337C | - | 660-D-4001 | PRESSURE REL | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | -1 | 15 |  | bar | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4337 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS453/P06 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660PI4337A | - | 660-D-4001 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4337 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660PI4337B | - | 660-D-4001 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4337 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 0 | - | 660PI4337C | - | 660-D-4001 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4337 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 0 | - | 660PSHH4337A | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 13.7 | bar | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4337 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 0 | - | 660PSHH4337B | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 13.7 | bar | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4337 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 9 | - | 0 | - | 660PSHH4337C | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 13.7 | bar | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4337 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 10 | - | 0 | - | 660PAH4337 | - | 660-D-4001 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | S-PLC | - |  |  | 13.2 | bar | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4337 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660PT4339 | - | 660 D 4006 | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 2 |  | bar | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4339 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJM409/P04 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660PI4339 | - | 660 D 4006 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4339 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660PC4339 | - | 660 D 4006 | CONTROLLER | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4339 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660PSH4339 | - | 660 D 4006 | SOFT THRESHOLD | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 1.5 | bar | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4339 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | CV01 | - | 5 | - | 0 | - | 660PV4339A | - | Nitrogen to 660 D 4006 | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4339 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJM409/P05 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | CV01 | - | 6 | - | 0 | - | 660PV4339B | - | Nitrogen to 660 D 4006 | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4339 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJM409/P06 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 0 | - | 660PY4339A | - | 660 D 4006 | SOFT CALCULATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4339 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 0 | - | 660PY4339B | - | 660 D 4006 | SOFT CALCULATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4339 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660PDI4340 | - | 660 D 4005 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4340 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660PDAH4340 | - | 660 D 4005 | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 2.5 | bar | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4340 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660PDT4340 | - | 660 D 4005 | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 4 |  | bar | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4340 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM409/P07 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660PT4341 | - | LPG TO BATTERY LIMITS | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 20 |  | bar | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4341 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJM402/P03 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660PI4341 | - | LPG TO BATTERY LIMITS | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4341 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660PC4341 | - | LPG TO BATTERY LIMITS | CONTROLLER | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4341 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | CV01 | - | 4 | - | 0 | - | 660PV4341A | - | LPG TO BATTERY LIMITS | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4341 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJM402/P04 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | CV01 | - | 5 | - | 0 | - | 660PV4341B | - | LPG TO BATTERY LIMITS | CONTROL VALVE | - | - | - | - | - | L | ST1C | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4341 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJM402/P05 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 0 | - | 660PY4341A | - | LPG TO BATTERY LIMITS | SOFT CALCULATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4341 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 0 | - | 660PY4341B | - | LPG TO BATTERY LIMITS | SOFT CALCULATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4341 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 0 | - | 660PI4341A | - | LPG TO BATTERY LIMITS | PRESSURE INDICATOR | - | - | - | - | - | L | ST1C | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4341 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJM402/P02 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660PTS4342 | - | 660 D 4006 | PRESSURE REL | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | 0 | 4 |  | bar | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4342 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS410/P02 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660PI4342 | - | 660 D 4006 | INDICATION | - | - | - | - | - | CRD | ST1D | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4342 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660PSHH4342 | - | 660 D 4006 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | SIS | S-PLC | - |  |  | 2 | bar | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4342 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660PAL4342 | - | 660 D 4006 | ALARM | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  | 0.5 | bar | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4342 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660PT4343 | - | HDT PURGE FROM 662C3001 | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 60 |  | bar | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4343 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM401/P13 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660PI4343 | - | HDT PURGE FROM 662C3001 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4343 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660PAH4343 | - | HDT PURGE FROM 662C3001 | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 42 | bar | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4343 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660PTS4344 | - | LPG FROM 660 D 4004 | PRESSURE REL | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | 0 | 10 |  | bar | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4344 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS408/P08 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660PI4344 | - | LPG FROM 660 D 4004 | INDICATION | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4344 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660PSLL4344 | - | LPG FROM 660 D 4004 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | SIS | S-PLC | - |  |  | 5.5 | bar | 214359C-6603-PID-0021-0409 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4344 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660PT4462 | - | METHANOL INJECTION PUMPS 660G4006A | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -1 | 20 |  | bar | FR-GPS-100-0-OMG-000003 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4462 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 662BJM130/P19 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660PI4462 | - | METHANOL INJECTION PUMPS 660G4006A | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | FR-GPS-100-0-OMG-000003 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4462 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660PAH4462 | - | METHANOL INJECTION PUMPS 660G4006A | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 3.5 | bar | FR-GPS-100-0-OMG-000003 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4462 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660PT4464 | - | METHANOL INJECTION PUMPS 660G4006B | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -1 | 20 |  | bar | FR-GPS-100-0-OMG-000003 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4464 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 662BJM130/P21 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660PI4464 | - | METHANOL INJECTION PUMPS 660G4006A | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | FR-GPS-100-0-OMG-000003 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4464 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660PAH4464 | - | METHANOL INJECTION PUMPS 660G4006A | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 3.5 | bar | FR-GPS-100-0-OMG-000003 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4464 | NbO1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660PTS4500 | - | 660K4001-PRESSURE SENSOR | PRESSURE REL | - | - | - | - | - | L | ST1C | MAINT | MMS | - | 0 | 25 |  | bar | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660P4500 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS458/P05 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660PTS4501 | - | 660K4001-PRESSURE SENSOR | PRESSURE REL | - | - | - | - | - | L | ST1C | MAINT | MMS | - | 0 | 25 |  | bar | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660P4501 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS458/P06 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660PTS4502 | - | 660K4001-PRESSURE SENSOR | PRESSURE REL | - | - | - | - | - | L | ST1C | MAINT | MMS | - | -1 | 100 |  | bar | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660P4502 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS458/P07 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660PTS4503 | - | 660K4001-PRESSURE SENSOR | PRESSURE REL | - | - | - | - | - | L | ST1C | MAINT | MMS | - | -1 | 100 |  | bar | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660P4503 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS458/P08 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660PTS4504A | - | 660-G-4002 | PRESSURE REL | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | -1 | 10 |  | bar | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4504 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS451/P07 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660PTS4504B | - | 660-G-4002 | PRESSURE REL | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | -1 | 10 |  | bar | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4504 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS452/P08 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660PTS4504C | - | 660-G-4002 | PRESSURE REL | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | -1 | 10 |  | bar | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4504 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS453/P07 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660PI4504A | - | 660-G-4002 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4504 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660PI4504B | - | 660-G-4002 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4504 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 0 | - | 660PI4504C | - | 660-G-4002 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4504 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 0 | - | 660PSLL4504A | - | 660-G-4002 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 2 | bar | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4504 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 10 | - | 0 | - | 660PSLL4504B | - | 660-G-4002 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 2 | bar | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4504 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 12 | - | 0 | - | 660PSLL4504C | - | 660-G-4002 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 2 | bar | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4504 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 14 | - | 0 | - | 660PSL4504 | - | 660-G-4002 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1C | BPCS/SIS | DCS | - |  |  | 2.5 | bar | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4504 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660PDT4506 | - | 660-D-4011A | PRESSURE DP | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -1 | 2.5 |  | bar | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4506 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM454/P02 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660PDI4506 | - | 660-D-4011A | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4506 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660PDAH4506 | - | 660-D-4011A | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 1.5 | bar | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4506 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660PTS4515A | - | FROM 660-E-4007A/B | PRESSURE REL | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | -1 | 10 |  | bar | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4515 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS451/P08 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660PTS4515B | - | FROM 660-E-4007A/B | PRESSURE REL | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | -1 | 10 |  | bar | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4515 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS452/P09 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660PTS4515C | - | FROM 660-E-4007A/B | PRESSURE REL | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | -1 | 10 |  | bar | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4515 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS453/P08 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660PI4515A | - | FROM 660-E-4007A/B | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4515 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660PI4515B | - | FROM 660-E-4007A/B | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4515 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 0 | - | 660PI4515C | - | FROM 660-E-4007A/B | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4515 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 0 | - | 660PSLL4515A | - | FROM 660-E-4007A/B | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 1.5 | bar | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4515 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 10 | - | 0 | - | 660PSLL4515B | - | FROM 660-E-4007A/B | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 1.5 | bar | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4515 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 12 | - | 0 | - | 660PSLL4515C | - | FROM 660-E-4007A/B | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 1.5 | bar | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4515 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 14 | - | 0 | - | 660PSL4515 | - | FROM 660-E-4007A/B | SOFT THRESHOLD | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | 2 | bar | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4515 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660PT4523 | - | Pressure Transmitter Nitrogen | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -1 | 10 |  | bar | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4523 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM454/P05 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660PI4523 | - | Pressure Transmitter Nitrogen | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4523 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660PAL4523 | - | Pressure Transmitter Nitrogen | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 0.6 | bar | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4523 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660PTS4526A | - | Leakage Gas | PRESSURE REL | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | -1 | 5 |  | bar | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4526 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS451/P09 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660PTS4526B | - | Leakage Gas | PRESSURE REL | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | -1 | 5 |  | bar | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4526 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS452/P10 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660PTS4526C | - | Leakage Gas | PRESSURE REL | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - | -1 | 5 |  | bar | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4526 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS453/P09 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660PI4526A | - | Leakage Gas | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4526 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660PI4526B | - | Leakage Gas | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4526 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 0 | - | 660PI4526C | - | Leakage Gas | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4526 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 0 | - | 660PSHH4526A | - | Leakage Gas | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 3 | bar | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4526 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 0 | - | 660PSLL4526A | - | Leakage Gas | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 0.1 | bar | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4526 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 9 | - | 0 | - | 660PSHH4526B | - | Leakage Gas | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 3 | bar | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4526 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 10 | - | 0 | - | 660PSLL4526B | - | Leakage Gas | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 0.1 | bar | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4526 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 11 | - | 0 | - | 660PSHH4526C | - | Leakage Gas | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 3 | bar | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4526 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 12 | - | 0 | - | 660PSLL4526C | - | Leakage Gas | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | BPCS/SIS | S-PLC | - |  |  | 0.1 | bar | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4526 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 14 | - | 0 | - | 660PAL4526 | - | Leakage Gas | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | 0.4 | bar | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4526 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 15 | - | 0 | - | 660PAH4526 | - | Leakage Gas | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | 2.5 | bar | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4526 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660PT4560 | - | HEFA OFF GAS TO SMR | PRESSURE TRANSMITTER | - | - | - | - | - | L | ST1C | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0041-0001 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4560 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660PI4560 | - | HEFA OFF GAS TO SMR | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0041-0001 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4560 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660PT4561 | - | LPG TO BATTERY LIMIT | PRESSURE TRANSMITTER | - | - | - | - | - | L | ST1C | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0041-0001 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4561 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660PI4561 | - | LPG TO BATTERY LIMIT | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0041-0001 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660P4561 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TE4001 | - | Cooling Water From 660-E-4001 | THERMOCOUPLE | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 214359C-6603-PID-0021-0403 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TI4001 | - | Cooling Water From 660-E-4001 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0403 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TT4001 | - | Cooling Water From 660-E-4001 | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 100 |  | °C | 214359C-6603-PID-0021-0403 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM411/P01 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660TW4001 | - | Cooling Water From 660-E-4001 | THERMOWELL | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 214359C-6603-PID-0021-0403 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4001 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TE4002 | - | Cooling Water From 660-E-4002 | THERMOCOUPLE | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 214359C-6603-PID-0021-0405 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4002 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TI4002 | - | Cooling Water From 660-E-4002 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0405 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4002 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TT4002 | - | Cooling Water From 660-E-4002 | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 100 |  | °C | 214359C-6603-PID-0021-0405 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4002 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM411/P02 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660TW4002 | - | Cooling Water From 660-E-4002 | THERMOWELL | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 214359C-6603-PID-0021-0405 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4002 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TTS4130A | - | 660-D-4001 | TEMPERATURE CONV | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | -50 | 200 |  | °C | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4130 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS451/P11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TTS4130B | - | 660-D-4001 | TEMPERATURE CONV | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | -50 | 200 |  | °C | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4130 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS452/P11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TTS4130C | - | 660-D-4001 | TEMPERATURE CONV | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | -50 | 200 |  | °C | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4130 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS453/P11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660TW4130A | - | 660-D-4001 | THERMOWELL | - | - | - | - | - | L | - | SIS | - | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4130 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660TW4130B | - | 660-D-4001 | THERMOWELL | - | - | - | - | - | L | - | SIS | - | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4130 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 0 | - | 660TW4130C | - | 660-D-4001 | THERMOWELL | - | - | - | - | - | L | - | SIS | - | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4130 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 0 | - | 660TE4130A | - | 660-D-4001 | RTD | - | - | - | - | - | L | - | SIS | - | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4130 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 0 | - | 660TE4130B | - | 660-D-4001 | RTD | - | - | - | - | - | L | - | SIS | - | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4130 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 9 | - | 0 | - | 660TE4130C | - | 660-D-4001 | RTD | - | - | - | - | - | L | - | SIS | - | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4130 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 10 | - | 0 | - | 660TI4130A | - | 660-D-4001 | INDICATION | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4130 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 11 | - | 0 | - | 660TI4130B | - | 660-D-4001 | INDICATION | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4130 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 12 | - | 0 | - | 660TI4130C | - | 660-D-4001 | INDICATION | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4130 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 13 | - | 0 | - | 660TSHH4130A | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | SIS | S-PLC | - |  |  | 140 | °C | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4130 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 14 | - | 0 | - | 660TSHH4130B | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | SIS | S-PLC | - |  |  | 140 | °C | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4130 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 15 | - | 0 | - | 660TSHH4130C | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | SIS | S-PLC | - |  |  | 140 | °C | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4130 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 16 | - | 0 | - | 660TAH4130 | - | 660-D-4001 | ALARM | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  | 130 | °C | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4130 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TTS4132A | - | 660-D-4001 | TEMPERATURE CONV | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | -50 | 200 |  | °C | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4132 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS451/P12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TTS4132B | - | 660-D-4001 | TEMPERATURE CONV | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | -50 | 200 |  | °C | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4132 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS452/P12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TTS4132C | - | 660-D-4001 | TEMPERATURE CONV | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | -50 | 200 |  | °C | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4132 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS453/P12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660TW4132A | - | 660-D-4001 | THERMOWELL | - | - | - | - | - | L | - | SIS | - | - |  |  |  |  | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4132 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660TW4132B | - | 660-D-4001 | THERMOWELL | - | - | - | - | - | L | - | SIS | - | - |  |  |  |  | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4132 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 0 | - | 660TW4132C | - | 660-D-4001 | THERMOWELL | - | - | - | - | - | L | - | SIS | - | - |  |  |  |  | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4132 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 0 | - | 660TE4132A | - | 660-D-4001 | RTD | - | - | - | - | - | L | - | SIS | - | - |  |  |  |  | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4132 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 0 | - | 660TE4132B | - | 660-D-4001 | RTD | - | - | - | - | - | L | - | SIS | - | - |  |  |  |  | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4132 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 9 | - | 0 | - | 660TE4132C | - | 660-D-4001 | RTD | - | - | - | - | - | L | - | SIS | - | - |  |  |  |  | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4132 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 10 | - | 0 | - | 660TI4132A | - | 660-D-4001 | INDICATION | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4132 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 11 | - | 0 | - | 660TI4132B | - | 660-D-4001 | INDICATION | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4132 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 12 | - | 0 | - | 660TI4132C | - | 660-D-4001 | INDICATION | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4132 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 13 | - | 0 | - | 660TSHH4132A | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | SIS | S-PLC | - |  |  | 140 | °C | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4132 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 14 | - | 0 | - | 660TSHH4132B | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | SIS | S-PLC | - |  |  | 140 | °C | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4132 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 15 | - | 0 | - | 660TSHH4132C | - | 660-D-4001 | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | SIS | S-PLC | - |  |  | 140 | °C | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4132 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 16 | - | 0 | - | 660TAH4132 | - | 660-D-4001 | ALARM | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - |  |  | 130 | °C | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4132 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TW4133 | - | 660-D-4001 | THERMOWELL | - | - | - | - | - | L | - | - | - | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4133 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TW4135 | - | 660-D-4001 | THERMOWELL | - | - | - | - | - | L | - | - | - | - |  |  |  |  | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4135 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TAH4137 | - | Wet Gas From 660-E-4001 To 660-D-4002 | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 45 | °C | 214359C-6603-PID-0021-0403 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4137 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TE4137 | - | Wet Gas From 660-E-4001 To 660-D-4002 | THERMOCOUPLE | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 214359C-6603-PID-0021-0403 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4137 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TI4137 | - | Wet Gas From 660-E-4001 To 660-D-4002 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0403 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4137 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660TT4137 | - | Wet Gas From 660-E-4001 To 660-D-4002 | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 100 |  | °C | 214359C-6603-PID-0021-0403 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4137 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM411/P03 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660TW4137 | - | Wet Gas From 660-E-4001 To 660-D-4002 | THERMOWELL | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 214359C-6603-PID-0021-0403 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4137 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TW4138 | - | LPG DRYER 660 D 4005 | THERMOWELL | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4138 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TE4138 | - | LPG DRYER 660 D 4005 | THERMOCOUPLE | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4138 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TT4138 | - | LPG DRYER 660 D 4005 | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 100 |  | °C | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4138 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM402/P06 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660TI4138 | - | LPG DRYER 660 D 4005 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4138 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660TAH4138 | - | LPG DRYER 660 D 4005 | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 50 | °C | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4138 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 0 | - | 660TI4138A | - | LPG DRYER 660 D 4005 | LOCAL INDICATOR | - | - | - | - | - | L | ST1C | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4138 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AO11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJM402/P09 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 0 | - | 660TAL4138 | - | LPG DRYER 660 D 4005 | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 15 | °C | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4138 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TE4139 | - | Wet Gas From 660-E-4002 To 660-D-4003 | THERMOCOUPLE | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 214359C-6603-PID-0021-0405 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4139 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TI4139 | - | Wet Gas From 660-E-4002 To 660-D-4003 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0405 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4139 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TT4139 | - | Wet Gas From 660-E-4002 To 660-D-4003 | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 100 |  | °C | 214359C-6603-PID-0021-0405 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4139 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM411/P04 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660TW4139 | - | Wet Gas From 660-E-4002 To 660-D-4003 | THERMOWELL | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 214359C-6603-PID-0021-0405 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4139 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660TAH4139 | - | Wet Gas From 660-E-4002 To 660-D-4003 | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 53 | °C | 214359C-6603-PID-0021-0405 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4139 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TW4140 | - | 660-D-4005 | THERMOWELL | - | - | - | - | - | L | - | - | - | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4140 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TW4141 | - | 660-E-4003 | THERMOWELL | - | - | - | - | - | L | - | SIS | - | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4141 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TE4141 | - | 660-E-4003 | RTD | - | - | - | - | - | L | - | SIS | - | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4141 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TTS4141 | - | 660-E-4003 | TEMPERATURE CONV | - | - | - | - | - | L | ST1D | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4141 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TW4142 | - | OFF GAS TO SMR | THERMOWELL | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4142 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TE4142 | - | OFF GAS TO SMR | THERMOCOUPLE | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4142 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TT4142 | - | OFF GAS TO SMR | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 150 |  | °C | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4142 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM401/P12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660TI4142 | - | OFF GAS TO SMR | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4142 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660TC4142 | - | OFF GAS TO SMR | CONTROLLER | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4142 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 0 | - | 660TAL4142 | - | OFF GAS TO SMR | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 55 | °C | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4142 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 0 | - | 660TAH4142 | - | OFF GAS TO SMR | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 65 | °C | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4142 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TW4143 | - | OFF GAS TO SMR | THERMOWELL | - | - | - | - | - | L | - | SIS | - | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4143 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TE4143 | - | OFF GAS TO SMR | THERMOCOUPLE | - | - | - | - | - | L | - | SIS | - | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4143 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TTS4143 | - | OFF GAS TO SMR | TEMPERATURE CONV | - | - | - | - | - | L | ST1D | SIS | S-PLC | - | 0 | 150 |  | °C | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4143 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS408/P06 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660TI4143 | - | OFF GAS TO SMR | INDICATION | - | - | - | - | - | CRD | SdC | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4143 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660TSLL4143 | - | OFF GAS TO SMR | SOFT THERSHOLD | - | - | - | - | - | ITR | ST1D | SIS | S-PLC | - |  |  | 50 | °C | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4143 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 7 | - | 0 | - | 660TSHH4143 | - | OFF GAS TO SMR | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | SIS | S-PLC | - |  |  | 75 | °C | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4143 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TW4145 | - | TO 660D4006 | THERMOWELL | - | - | - | - | - | L | - |  | - | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4145 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TW4146 | - | 660-D-4001 | THERMOWELL | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4146 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TE4146 | - | 660-D-4001 | RTD | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4146 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TT4146 | - | 660-D-4001 | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -50 | 200 |  | °C | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4146 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM454/P06 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660TI4146 | - | 660-D-4001 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4146 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660TAH4146 | - | 660-D-4001 | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 70 | °C | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4146 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 0 | - | 660TAL4146 | - | 660-D-4001 | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 30 | °C | 660-3-TENV-006001 - 1 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4146 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TW4147 | - | 660-D-4001 | THERMOWELL | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4147 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TE4147 | - | 660-D-4001 | RTD | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4147 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TT4147 | - | 660-D-4001 | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -50 | 200 |  | °C | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4147 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM454/P07 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660TI4147 | - | 660-D-4001 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4147 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660TAH4147 | - | 660-D-4001 | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 70 | °C | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4147 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 0 | - | 660TAL4147 | - | 660-D-4001 | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 30 | °C | 660-3-TENV-006001 - 2 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4147 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TT4237 | - | STEAM TO 660-E-4004 | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 300 |  | °C | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4237 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM401/P16 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TI4237 | - | STEAM TO 660-E-4004 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4237 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TW4237 | - | STEAM TO 660-E-4004 | THERMOWELL | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4237 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660TE4237 | - | STEAM TO 660-E-4004 | THERMOCOUPLE | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4237 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TW4343 | - | LPG TO BATTERY LIMITS | THERMOWELL | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4343 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TE4343 | - | LPG TO BATTERY LIMITS | THERMOCOUPLE | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4343 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TT4343 | - | LPG TO BATTERY LIMITS | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | BPCS | DCS | - | 0 | 100 |  | °C | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4343 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM402/P10 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660TI4343 | - | LPG TO BATTERY LIMITS | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4343 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660TAL4343 | - | LPG TO BATTERY LIMITS | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 5 | °C | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4343 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TE4500 | - | Temperature Transmitter Compressor Main Bearing NDE | RTD | - | - | - | - | - | L | - | MAINT | MMS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4500 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TTS4500 | - | Temperature Transmitter Compressor Main Bearing NDE | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | MAINT | MMS | - | -50 | 200 |  | °C | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4500 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS457/P01 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TAH4500 | - | Temperature Transmitter Compressor Main Bearing NDE | ALARM | - | - | - | - | - | CRD | ST1C | MAINT | MMS | - |  |  | 80 | °C | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4500 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660TS4500 | - | Temperature Transmitter Compressor Main Bearing NDE | CONTACT | - | - | NORMALLY CLOSE | - | - | ITR | ST1D | MAINT | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | FROM ST1C / MMS | - | - | - | - | 660T4500 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | By OSBL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660TSHH4500 | - | Temperature Transmitter Compressor Main Bearing NDE | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | MAINT | MMS | - |  |  | 90 | °C | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4500 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TE4501 | - | Temperature Transmitter Compressor Main Bearing NDE | RTD | - | - | - | - | - | L | - | MAINT | MMS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4501 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TTS4501 | - | Temperature Transmitter Compressor Main Bearing NDE | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | MAINT | MMS | - | -50 | 200 |  | °C | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4501 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS457/P02 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TAH4501 | - | Temperature Transmitter Compressor Main Bearing NDE | ALARM | - | - | - | - | - | CRD | ST1C | MAINT | MMS | - |  |  | 80 | °C | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4501 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660TSHH4501 | - | Temperature Transmitter Compressor Main Bearing NDE | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1D | MAINT | MMS | - |  |  | 90 | °C | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4501 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TE4502 | - | 660K4001-CROSSHEAD PIN & BIG END TEMPERATURE SENSOR | RTD | - | - | - | - | - | L | - | MAINT | MMS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4502 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TTS4502 | - | 660K4001-CROSSHEAD PIN & BIG END TEMPERATURE SENSOR | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | MAINT | MMS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4502 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TAH4502 | - | 660K4001-CROSSHEAD PIN & BIG END TEMPERATURE SENSOR | ALARM | - | - | - | - | - | CRD | ST1C | MAINT | MMS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4502 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TE4503 | - | 660K4001-CROSSHEAD PIN & BIG END TEMPERATURE SENSOR | RTD | - | - | - | - | - | L | - | MAINT | MMS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4503 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TTS4503 | - | 660K4001-CROSSHEAD PIN & BIG END TEMPERATURE SENSOR | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | MAINT | MMS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4503 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TE4504 | - | 660K4001-PACKING TEMPERATURE | RTD | - | - | - | - | - | L | - | MAINT | MMS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4504 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TTS4504 | - | 660K4001-PACKING TEMPERATURE | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | MAINT | MMS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4504 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TE4505 | - | 660K4001-PACKING TEMPERATURE | RTD | - | - | - | - | - | L | - | MAINT | MMS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4505 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TT4505 | - | 660K4001-PACKING TEMPERATURE | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | MAINT | MMS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4505 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TE4506 | - | Temperature Cylinder Valve CE 1st Stage Suction | RTD | - | - | - | - | - | L | - | MAINT | MMS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4506 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TTS4506 | - | Temperature Cylinder Valve CE 1st Stage Suction | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | MAINT | MMS | - | -50 | 200 |  | °C | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4506 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS457/P03 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TAH4506 | - | Temperature Cylinder Valve CE 1st Stage Suction | ALARM | - | - | - | - | - | CRD | ST1C | MAINT | MMS | - |  |  | 130 | °C | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4506 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TE4507 | - | Temperature Cylinder Valve CE 1st Stage Suction | RTD | - | - | - | - | - | L | - | MAINT | MMS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4507 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TTS4507 | - | Temperature Cylinder Valve CE 1st Stage Suction | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | MAINT | MMS | - | -50 | 200 |  | °C | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4507 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS457/P04 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TAH4507 | - | Temperature Cylinder Valve CE 1st Stage Suction | ALARM | - | - | - | - | - | CRD | ST1C | MAINT | MMS | - |  |  | 130 | °C | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4507 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TE4508 | - | Temperature Cylinder Valve HE 1st Stage Suction | RTD | - | - | - | - | - | L | - | MAINT | MMS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4508 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TTS4508 | - | Temperature Cylinder Valve HE 1st Stage Suction | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | MAINT | MMS | - | -50 | 200 |  | °C | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4508 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS457/P05 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TAH4508 | - | Temperature Cylinder Valve HE 1st Stage Suction | ALARM | - | - | - | - | - | CRD | ST1C | MAINT | MMS | - |  |  | 130 | °C | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4508 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TE4509 | - | Temperature Cylinder Valve HE 1st Stage Suction | RTD | - | - | - | - | - | L | - | MAINT | MMS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4509 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TTS4509 | - | Temperature Cylinder Valve HE 1st Stage Suction | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | MAINT | MMS | - | -50 | 200 |  | °C | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4509 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS457/P06 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TAH4509 | - | Temperature Cylinder Valve HE 1st Stage Suction | ALARM | - | - | - | - | - | CRD | ST1C | MAINT | MMS | - |  |  | 130 | °C | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4509 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TE4510 | - | Temperature Cylinder Valve CE 1st Stage Discharge | RTD | - | - | - | - | - | L | - | MAINT | MMS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4510 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TTS4510 | - | Temperature Cylinder Valve CE 1st Stage Discharge | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | MAINT | MMS | - | -50 | 200 |  | °C | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4510 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS457/P07 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TAH4510 | - | Temperature Cylinder Valve CE 1st Stage Discharge | ALARM | - | - | - | - | - | CRD | ST1C | MAINT | MMS | - |  |  | 130 | °C | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4510 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TE4511 | - | Temperature Cylinder Valve CE 1st Stage Discharge | RTD | - | - | - | - | - | L | - | MAINT | MMS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4511 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TTS4511 | - | Temperature Cylinder Valve CE 1st Stage Discharge | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | MAINT | MMS | - | -50 | 200 |  | °C | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4511 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS457/P08 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TAH4511 | - | Temperature Cylinder Valve CE 1st Stage Discharge | ALARM | - | - | - | - | - | CRD | ST1C | MAINT | MMS | - |  |  | 130 | °C | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4511 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TE4512 | - | Temperature Cylinder Valve HE 1st Stage Discharge | RTD | - | - | - | - | - | L | - | MAINT | MMS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4512 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TTS4512 | - | Temperature Cylinder Valve HE 1st Stage Discharge | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | MAINT | MMS | - | -50 | 200 |  | °C | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4512 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS457/P09 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TAH4512 | - | Temperature Cylinder Valve HE 1st Stage Discharge | ALARM | - | - | - | - | - | CRD | ST1C | MAINT | MMS | - |  |  | 130 | °C | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4512 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TE4513 | - | Temperature Cylinder Valve HE 1st Stage Discharge | RTD | - | - | - | - | - | L | - | MAINT | MMS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4513 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TTS4513 | - | Temperature Cylinder Valve HE 1st Stage Discharge | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | MAINT | MMS | - | -50 | 200 |  | °C | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4513 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS457/P10 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TAH4513 | - | Temperature Cylinder Valve HE 1st Stage Discharge | ALARM | - | - | - | - | - | CRD | ST1C | MAINT | MMS | - |  |  | 130 | °C | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4513 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TE4514 | - | Temperature Cylinder Valve HE 2nd Stage Suction | RTD | - | - | - | - | - | L | - | MAINT | MMS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4514 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TTS4514 | - | Temperature Cylinder Valve HE 2nd Stage Suction | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | MAINT | MMS | - | -50 | 200 |  | °C | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4514 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS457/P11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TAH4514 | - | Temperature Cylinder Valve HE 2nd Stage Suction | ALARM | - | - | - | - | - | CRD | ST1C | MAINT | MMS | - |  |  | 130 | °C | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4514 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TE4515 | - | Temperature Cylinder Valve CE 2nd Stage Suction | RTD | - | - | - | - | - | L | - | MAINT | MMS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4515 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TTS4515 | - | Temperature Cylinder Valve CE 2nd Stage Suction | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | MAINT | MMS | - | -50 | 200 |  | °C | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4515 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS457/P12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TAH4515 | - | Temperature Cylinder Valve CE 2nd Stage Suction | ALARM | - | - | - | - | - | CRD | ST1C | MAINT | MMS | - |  |  | 130 | °C | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4515 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TE4516 | - | Temperature Cylinder Valve CE 2nd Stage Suction | RTD | - | - | - | - | - | L | - | MAINT | MMS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4516 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TTS4516 | - | Temperature Cylinder Valve CE 2nd Stage Suction | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | MAINT | MMS | - | -50 | 200 |  | °C | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4516 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS457/P13 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TAH4516 | - | Temperature Cylinder Valve CE 2nd Stage Suction | ALARM | - | - | - | - | - | CRD | ST1C | MAINT | MMS | - |  |  | 130 | °C | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4516 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TE4517 | - | Temperature Cylinder Valve CE 2nd Stage Discharge | RTD | - | - | - | - | - | L | - | MAINT | MMS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4517 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TTS4517 | - | Temperature Cylinder Valve CE 2nd Stage Discharge | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | MAINT | MMS | - | -50 | 200 |  | °C | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4517 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS457/P14 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TAH4517 | - | Temperature Cylinder Valve CE 2nd Stage Discharge | ALARM | - | - | - | - | - | CRD | ST1C | MAINT | MMS | - |  |  | 130 | °C | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4517 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TE4518 | - | Temperature Main Motor Bearing DE | RTD | - | - | - | - | - | L | - | MAINT | MMS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4518 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TTS4518 | - | Temperature Main Motor Bearing DE | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | MAINT | MMS | - | -50 | 200 |  | °C | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4518 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS457/P15 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TAH4518 | - | Temperature Main Motor Bearing DE | ALARM | - | - | - | - | - | CRD | ST1C | MAINT | MMS | - |  |  | 90 | °C | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4518 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TE4519 | - | Temperature Main Motor Bearing DE | RTD | - | - | - | - | - | L | - | MAINT | MMS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4519 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TTS4519 | - | Temperature Main Motor Bearing DE | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | MAINT | MMS | - | -50 | 200 |  | °C | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4519 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI12 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS457/P16 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TAH4519 | - | Temperature Main Motor Bearing DE | ALARM | - | - | - | - | - | CRD | ST1C | MAINT | MMS | - |  |  | 90 | °C | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4519 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TE4520 | - | Temperature Main Motor Bearing DE | RTD | - | - | - | - | - | L | P12 | MAINT | MOT | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4520 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TE4521 | - | Temperature Main Motor Bearing DE | RTD | - | - | - | - | - | L | P12 | MAINT | MOT | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660T4521 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TE4522 | - | Temperature Main Motor Bearing DE | RTD | - | - | - | - | - | L | P12 | MAINT | MOT | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | MOTOR | - | - | - | - | 660T4522 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TE4523 | - | 660K4001-MOTOR BEARING TEMP. SENSOR | RTD | - | - | - | - | - | L | ST1C | MAINT | MMS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | MOTOR | - | - | - | - | 660T4523 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI40 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TE4524 | - | 660K4001-MOTOR BEARING TEMP. SENSOR | RTD | - | - | - | - | - | L | ST1C | MAINT | MMS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | MOTOR | - | - | - | - | 660T4524 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI40 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TE4525 | - | 660K4001-MOTOR BEARING TEMP. SENSOR | RTD | - | - | - | - | - | L | ST1C | MAINT | MMS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | MOTOR | - | - | - | - | 660T4525 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI40 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TW4528 | - | 660-E-4005B | THERMOWELL | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4528 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TE4528 | - | 660-E-4005B | RTD | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4528 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TT4528 | - | 660-E-4005B | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -50 | 200 |  | °C | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4528 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM454/P08 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660TI4528 | - | 660-E-4005B | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4528 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660TAH4528 | - | 660-E-4005B | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 40 | °C | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4528 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TW4529 | - | 660-G-4003 | THERMOWELL | - | - | - | - | - | L | - | - | - | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4529 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TW4531 | - | 660-D-4011A | THERMOWELL | - | - | - | - | - | L | - | - | - | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4531 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TW4532 | - | 660-D-4011A | THERMOWELL | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4532 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TE4532 | - | 660-D-4011A | RTD | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4532 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TT4532 | - | 660-D-4011A | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -50 | 200 |  | °C | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4532 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM454/P09 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660TI4532 | - | 660-D-4011A | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4532 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660TAH4532 | - | 660-D-4011A | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 60 | °C | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4532 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 0 | - | 660TAL4532 | - | 660-D-4011A | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 10 | °C | 660-3-TENV-006001- 3 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4532 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TW4533 | - | TO 660-E-4007A/B | THERMOWELL | - | - | - | - | - | L | - | - | - | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4533 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TW4534 | - | TO 660-E-4007A/B | THERMOWELL | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4534 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TE4534 | - | TO 660-E-4007A/B | RTD | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4534 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TT4534 | - | TO 660-E-4007A/B | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -50 | 200 |  | °C | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4534 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM454/P10 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660TI4534 | - | TO 660-E-4007A/B | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4534 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660TAH4534 | - | TO 660-E-4007A/B | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 40 | °C | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4534 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TW4536 | - | TO 660-E-4007A/B | THERMOWELL | - | - | - | - | - | L | - | - | - | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4536 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TW4537 | - | FROM 660-E-4007A/B | THERMOWELL | - | - | - | - | - | L | - | - | - | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4537 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TW4538 | - | FROM 660-E-4007A/B | THERMOWELL | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4538 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TE4538 | - | FROM 660-E-4007A/B | RTD | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4538 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TT4538 | - | FROM 660-E-4007A/B | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -50 | 200 |  | °C | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4538 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM454/P11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660TI4538 | - | FROM 660-E-4007A/B | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4538 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660TAH4538 | - | FROM 660-E-4007A/B | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 65 | °C | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4538 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 0 | - | 660TAL4538 | - | FROM 660-E-4007A/B | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 43 | °C | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4538 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TW4541 | - | TO 660-E-4008 | THERMOWELL | - | - | - | - | - | L | - | - | - | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4541 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TW4542 | - | TO 660-E-4008 | THERMOWELL | - | - | - | - | - | L | - | - | - | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4542 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TW4543 | - | TO 660-E-4008 | THERMOWELL | - | - | - | - | - | L | - | - | - | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4543 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TW4544 | - | TO 660-D-4010 | THERMOWELL | - | - | - | - | - | L | - | - | - | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4544 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TW4545 | - | TO 660-D-4010 | THERMOWELL | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4545 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TE4545 | - | TO 660-D-4010 | RTD | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4545 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TT4545 | - | TO 660-D-4010 | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -50 | 200 |  | °C | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4545 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM454/P12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660TI4545 | - | TO 660-D-4010 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4545 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660TAH4545 | - | TO 660-D-4010 | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 65 | °C | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4545 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 6 | - | 0 | - | 660TAL4545 | - | TO 660-D-4010 | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 48 | °C | 660-3-TENV-006001- 4 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4545 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TW4546 | - | Leakage Gas Packing 2nd Stage | THERMOWELL | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4546 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TE4546 | - | Leakage Gas Packing 2nd Stage | RTD | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4546 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TT4546 | - | Leakage Gas Packing 2nd Stage | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -50 | 200 |  | °C | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4546 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM454/P13 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660TI4546 | - | Leakage Gas Packing 2nd Stage | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4546 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660TAH4546 | - | Leakage Gas Packing 2nd Stage | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 100 | °C | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4546 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660TW4547 | - | Leakage Gas Packing 1st Stage | THERMOWELL | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4547 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660TE4547 | - | Leakage Gas Packing 1st Stage | RTD | - | - | - | - | - | L | - | BPCS | - | - |  |  |  |  | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4547 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660TT4547 | - | Leakage Gas Packing 1st Stage | TEMPERATURE CONV | - | - | - | - | - | L | ST1C | BPCS | DCS | - | -50 | 200 |  | °C | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4547 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM454/P14 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660TI4547 | - | Leakage Gas Packing 1st Stage | INDICATION | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4547 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660TAH4547 | - | Leakage Gas Packing 1st Stage | ALARM | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  | 100 | °C | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660T4547 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 1 | - | 0 | - | 660UVS4155 | - | FROM 660-D-4001 | ON OFF VALVE | - | - | - | - | - | L | - | BPCS/SIS | - | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4155 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 2 | - | 0 | - | 660UYS4155 | - | FROM 660-D-4001 | AIR SOLENOID SPRING | - | - | WITH ON OFF VALVE | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4155 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJCS414/C03-C04 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 3 | - | 0 | - | 660UZSL4155 | - | FROM 660-D-4001 | LIMIT SWITCH INDUCTIVE | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4155 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS412/P02 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 4 | - | 0 | - | 660UZSH4155 | - | FROM 660-D-4001 | LIMIT SWITCH INDUCTIVE | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4155 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS412/P01 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 6 | - | 0 | - | 660HS4155D | - | FROM 660-D-4001 | PB SOFT | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4155 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 7 | - | 0 | - | 660HS4155A | - | FROM 660-D-4001 | ESD PB | - | - | NORMALLY CLOSE | - | - | CRA | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4155 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | By OSBL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 8 | - | 0 | - | 660HS4155B | - | FROM 660-D-4001 | ESD PB | - | - | NORMALLY CLOSE | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4155 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS412/P16 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 9 | - | 0 | - | 660HS4155C | - | FROM 660-D-4001 | ESD PB | - | - | NORMALLY CLOSE | - | - | CRA | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4155 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | By OSBL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 10 | - | 0 | - | 660XL4155 | - | FROM 660-D-4001 | LIGHT | - | - | - | - | - | CRA | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4155 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | By OSBL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 11 | - | 0 | - | 660PT4155 | - | FROM 660-D-4001 - VALVE AIR RESERVE | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS/SIS | DCS | - | 0 | 10 |  | bar | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4155 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM406/P09 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 12 | - | 0 | - | 660PI4155 | - | FROM 660-D-4001 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4155 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 13 | - | 0 | - | 660PAL4155 | - | FROM 660-D-4001 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | 4.5 | bar | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4155 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 1 | - | 0 | - | 660UVS4156 | - | FROM 660-D-4001 | ON OFF VALVE | - | - | - | - | - | L | - | BPCS/SIS | - | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4156 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 2 | - | 0 | - | 660UYS4156 | - | FROM 660-D-4001 | AIR SOLENOID SPRING | - | - | WITH ON OFF VALVE | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4156 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJCS414/C07-C08 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 3 | - | 0 | - | 660HLS4156 | - | FROM 660-D-4001 | TPL OPEN/CLOSE | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4156 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 4 | - | 0 | - | 660UZSL4156 | - | FROM 660-D-4001 | LIMIT SWITCH INDUCTIVE | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4156 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS412/P04 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 5 | - | 0 | - | 660UZSH4156 | - | FROM 660-D-4001 | LIMIT SWITCH INDUCTIVE | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4156 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS412/P03 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 7 | - | 0 | - | 660PT4156 | - | FROM 660-D-4001- VALVE AIR RESERVE | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS/SIS | DCS | - | 0 | 10 |  | bar | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4156 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM406/P10 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 8 | - | 0 | - | 660PI4156 | - | FROM 660-D-4001 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4156 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 9 | - | 0 | - | 660PAL4156 | - | FROM 660-D-4001 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | 4.5 | bar | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4156 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 1 | - | 0 | - | 660UVS4157 | - | FROM 660-D-4001 | ON OFF VALVE | - | - | - | - | - | L | - | BPCS/SIS | - | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4157 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 2 | - | 0 | - | 660UYS4157 | - | FROM 660-D-4001 | AIR SOLENOID SPRING | - | - | WITH ON OFF VALVE | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4157 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJCS414/C05-C06 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 3 | - | 0 | - | 660HLS4157 | - | FROM 660-D-4001 | TPL OPEN/CLOSE | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4157 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 4 | - | 0 | - | 660UZSL4157 | - | FROM 660-D-4001 | LIMIT SWITCH INDUCTIVE | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4157 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS412/P06 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 5 | - | 0 | - | 660UZSH4157 | - | FROM 660-D-4001 | LIMIT SWITCH INDUCTIVE | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4157 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS412/P05 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 7 | - | 0 | - | 660PT4157 | - | FROM 660-D-4001 - VALVE AIR RESERVE | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS/SIS | DCS | - | 0 | 10 |  | bar | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4157 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM406/P11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 8 | - | 0 | - | 660PI4157 | - | FROM 660-D-4001 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4157 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 9 | - | 0 | - | 660PAL4157 | - | FROM 660-D-4001 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | 4.5 | bar | 214359C-6603-PID-0021-0401 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4157 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 1 | - | 0 | - | 660UVS4159 | - | FROM 660-D-4002 | ON OFF VALVE | - | - | - | - | - | L | - | BPCS/SIS | - | - |  |  |  |  | 214359C-6603-PID-0021-0404 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4159 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 3 | - | 0 | - | 660UYS4159 | - | FROM 660-D-4002 | AIR SOLENOID SPRING | - | - | WITH ON OFF VALVE | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0404 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4159 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJCS414/C09-C10 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 4 | - | 0 | - | 660HLS4159 | - | FROM 660-D-4002 | TPL START/STOP | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0404 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4159 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 5 | - | 0 | - | 660UZSL4159 | - | FROM 660-D-4002 | LIMIT SWITCH INDUCTIVE | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0404 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4159 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS412/P08 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 6 | - | 0 | - | 660UZSH4159 | - | FROM 660-D-4002 | LIMIT SWITCH INDUCTIVE | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0404 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4159 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS412/P07 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 8 | - | 0 | - | 660PT4159 | - | FROM 660-D-4002 - VALVE AIR RESERVE | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS/SIS | DCS | - | 0 | 10 |  | bar | 214359C-6603-PID-0021-0404 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4159 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM406/P12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 9 | - | 0 | - | 660PI4159 | - | FROM 660-D-4002 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0404 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4159 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 10 | - | 0 | - | 660PAL4159 | - | FROM 660-D-4002 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | 4.5 | bar | 214359C-6603-PID-0021-0404 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4159 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 1 | - | 0 | - | 660UVS4160 | - | FROM 660-D-4003 | ON OFF VALVE | - | - | - | - | - | L | - | BPCS/SIS | - | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4160 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 2 | - | 0 | - | 660UYS4160 | - | FROM 660-D-4003 | AIR SOLENOID SPRING | - | - | SOLENOID ONLY | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4160 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJCS419/C01-C02 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 3 | - | 0 | - | 660UZSL4160 | - | FROM 660-D-4003 | LIMIT SWITCH INDUCTIVE | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4160 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS413/P02 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 4 | - | 0 | - | 660UZSH4160 | - | FROM 660-D-4003 | LIMIT SWITCH INDUCTIVE | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4160 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS413/P01 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 6 | - | 0 | - | 660HS4160D | - | FROM 660-D-4003 | PB SOFT | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4160 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 7 | - | 0 | - | 660HS4160A | - | FROM 660-D-4003 | ESD PB | - | - | NORMALLY CLOSE | - | - | CRA | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4160 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | By OSBL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 8 | - | 0 | - | 660HS4160B | - | FROM 660-D-4003 | ESD PB | - | - | NORMALLY CLOSE | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4160 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS423/P01 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 9 | - | 0 | - | 660HS4160C | - | FROM 660-D-4003 | ESD PB | - | - | NORMALLY OPEN | - | - | CRA | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4160 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | By OSBL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 10 | - | 0 | - | 660XL4160 | - | FROM 660-D-4003 | LIGHT | - | - | - | - | - | CRA | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4160 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | By OSBL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 11 | - | 0 | - | 660PT4160 | - | FROM 660-D-4003 - VALVE AIR RESERVE | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS/SIS | DCS | - | 0 | 10 |  | bar | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4160 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM403/P06 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 12 | - | 0 | - | 660PI4160 | - | FROM 660-D-4003 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4160 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 13 | - | 0 | - | 660PAL4160 | - | FROM 660-D-4003 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | 4.5 | bar | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4160 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 1 | - | 0 | - | 660UVS4161 | - | FROM 660-D-4003 | ON OFF VALVE | - | - | - | - | - | L | - | BPCS/SIS | - | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4161 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 2 | - | 0 | - | 660UYS4161 | - | FROM 660-D-4003 | AIR SOLENOID SPRING | - | - | SOLENOID ONLY | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4161 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJCS414/C01-C02 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 3 | - | 0 | - | 660HLS4161 | - | FROM 660-D-4003 | TPL OPEN/CLOSE | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4161 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 4 | - | 0 | - | 660UZSL4161 | - | FROM 660-D-4003 | LIMIT SWITCH INDUCTIVE | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4161 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS412/P10 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 5 | - | 0 | - | 660UZSH4161 | - | FROM 660-D-4003 | LIMIT SWITCH INDUCTIVE | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4161 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS412/P09 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 7 | - | 0 | - | 660PT4161 | - | FROM 660-D-4003 - VALVE AIR RESERVE | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS/SIS | DCS | - | 0 | 10 |  | bar | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4161 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM406/P13 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 8 | - | 0 | - | 660PI4161 | - | FROM 660-D-4003 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4161 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 9 | - | 0 | - | 660PAL4161 | - | FROM 660-D-4003 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | 4.5 | bar | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4161 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 1 | - | 0 | - | 660UVS4162 | - | LPG TO BATTERY LIMITS | ON OFF VALVE | - | - | - | - | - | L | - | BPCS/SIS | - | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4162 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 2 | - | 0 | - | 660UYS4162 | - | LPG TO BATTERY LIMITS | AIR SOLENOID SPRING | - | - | SOLENOID ONLY | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4162 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJCS420/C01-C02 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 3 | - | 0 | - | 660HLS4162 | - | LPG TO BATTERY LIMITS | TPL OPEN / CLOSE | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4162 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 4 | - | 0 | - | 660UZSL4162 | - | LPG TO BATTERY LIMITS | LIMIT SWITCH INDUCTIVE | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4162 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS415/P02 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 5 | - | 0 | - | 660UZSH4162 | - | LPG TO BATTERY LIMITS | LIMIT SWITCH INDUCTIVE | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4162 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS415/P01 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 7 | - | 0 | - | 660PT4162 | - | LPG TO BATTERY LIMITS | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS/SIS | DCS | - | 0 | 10 |  | bar | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4162 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM402/P07 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 8 | - | 0 | - | 660PI4162 | - | LPG TO BATTERY LIMITS | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4162 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 9 | - | 0 | - | 660PAL4162 | - | LPG TO BATTERY LIMITS | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | 4.5 | bar | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4162 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 1 | - | 0 | - | 660UVS4163 | - | HP LPG Separator Gas Product to Gas to SMR Heater | ON OFF VALVE | - | - | - | - | - | L | - | BPCS/SIS | - | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4163 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 2 | - | 0 | - | 660UYS4163 | - | FROM 660-D-4003 | AIR SOLENOID SPRING | - | - | SOLENOID ONLY | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4163 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 3 | - | 0 | - | 660HLS4163 | - | FROM 660-D-4003 | TPL OPEN/CLOSE | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4163 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 4 | - | 0 | - | 660UZSL4163 | - | UVS4163 CLOSE | LIMIT SWITCH INDUCTIVE | - | - | INDUCTIVE | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4163 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 5 | - | 0 | - | 660UZSH4163 | - | UVS4163 OPEN | LIMIT SWITCH INDUCTIVE | - | - | INDUCTIVE | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4163 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 7 | - | 0 | - | 660PT4163 | - | FROM 660-D-4003 - VALVE AIR RESERVE | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4163 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 8 | - | 0 | - | 660PI4163 | - | FROM 660-D-4003 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4163 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 9 | - | 0 | - | 660PAL4163 | - | FROM 660-D-4003 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4163 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 1 | - | 0 | - | 660UVS4164 | - | LPG FROM 660 G 4001 A/B | ON OFF VALVE | - | - | - | - | - | L | - | BPCS/SIS | - | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4164 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 2 | - | 0 | - | 660UYS4164 | - | On-ff Valve 660UVS4164 | AIR SOLENOID SPRING | - | - | SOLENOID ONLY | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4164 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJCS421/C01-C02 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 3 | - | 0 | - | 660HLS4164 | - | LPG FROM 660 G 4001 A/B | TPL OPEN/CLOSE | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4164 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 4 | - | 0 | - | 660UZSL4164 | - | LPG FROM 660 G 4001 A/B | LIMIT SWITCH INDUCTIVE | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4164 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS416/P02 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 5 | - | 0 | - | 660UZSH4164 | - | LPG FROM 660 G 4001 A/B | LIMIT SWITCH INDUCTIVE | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4164 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS416/P01 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 7 | - | 0 | - | 660PT4164 | - | LPG FROM 660 G 4001 A/B | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS/SIS | DCS | - | 0 | 10 |  | bar | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4164 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM409/P08 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 8 | - | 0 | - | 660PI4164 | - | LPG FROM 660 G 4001 A/B | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4164 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 9 | - | 0 | - | 660PAL4164 | - | LPG FROM 660 G 4001 A/B | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | 4.5 | bar | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4164 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 1 | - | 0 | - | 660UVS4165 | - | LPG Dryer depressuring | ON OFF VALVE | - | - | - | - | - | L | - | BPCS/SIS | - | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4165 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 2 | - | 0 | - | 660UYS4165 | - | LPG Dryer depressuring | AIR SOLENOID SPRING | - | - | SOLENOID ONLY | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4165 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJCS420/C03-C04 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 3 | - | 0 | - | 660UZSL4165 | - | LPG Dryer depressuring | LIMIT SWITCH INDUCTIVE | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4165 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS415/P04 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 4 | - | 0 | - | 660UZSH4165 | - | LPG Dryer depressuring | LIMIT SWITCH INDUCTIVE | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4165 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS415/P03 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 6 | - | 0 | - | 660HS4165D | - | LPG Dryer depressuring | PB SOFT | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4165 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 7 | - | 0 | - | 660HS4165A | - | LPG Dryer depressuring | ESD PB | - | - | NORMALLY CLOSE | - | - | CRA | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4165 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | By OSBL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 8 | - | 0 | - | 660HS4165B | - | LPG Dryer depressuring | ESD PB | - | - | NORMALLY CLOSE | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4165 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS415/P05 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 9 | - | 0 | - | 660HS4165C | - | LPG Dryer depressuring | ESD PB | - | - | NORMALLY OPEN | - | - | CRA | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4165 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | By OSBL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 10 | - | 0 | - | 660XL4165 | - | LPG Dryer depressuring | LIGHT | - | - | - | - | - | CRA | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4165 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | By OSBL | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 11 | - | 0 | - | 660PT4165 | - | LPG Dryer depressuring | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS/SIS | DCS | - | 0 | 10 |  | bar | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4165 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM402/P08 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 12 | - | 0 | - | 660PI4165 | - | LPG Dryer depressuring | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4165 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV09 | - | 13 | - | 0 | - | 660PAL4165 | - | LPG Dryer depressuring | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | 4.5 | bar | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4165 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 1 | - | 0 | - | 660UVS4166 | - | TO SWS | ON OFF VALVE | - | - | - | - | - | L | - | BPCS/SIS | - | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4166 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 2 | - | 0 | - | 660UYS4166 | - | TO SWS | AIR SOLENOID SPRING | - | - | SOLENOID ONLY | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4166 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJCS418/C03-C04 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 3 | - | 0 | - | 660HLS4166 | - | TO SWS | TPL OPEN/CLOSE | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4166 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 4 | - | 0 | - | 660UZSL4166 | - | TO SWS | LIMIT SWITCH INDUCTIVE | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4166 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS417/P02 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 5 | - | 0 | - | 660UZSH4166 | - | TO SWS | LIMIT SWITCH INDUCTIVE | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4166 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS417/P01 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 7 | - | 0 | - | 660PT4166 | - | TO SWS - VALVE AIR RESERVE | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS/SIS | DCS | - | 0 | 10 |  | bar | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4166 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM401/P07 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 8 | - | 0 | - | 660PI4166 | - | TO SWS | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4166 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 9 | - | 0 | - | 660PAL4166 | - | TO SWS | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | 4.5 | bar | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4166 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 1 | - | 0 | - | 660UVS4167 | - | LPG TO 660 G 4001 A/B | ON OFF VALVE | - | - | - | - | - | L | - | BPCS/SIS | - | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4167 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 2 | - | 0 | - | 660UYS4167 | - | LPG TO 660 G 4001 A/B | AIR SOLENOID SPRING | - | - | SOLENOID ONLY | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4167 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJCS418/C05-C06 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 3 | - | 0 | - | 660HLS4167 | - | LPG TO 660 G 4001 A/B | TPL OPEN/CLOSE | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4167 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 4 | - | 0 | - | 660UZSL4167 | - | LPG TO 660 G 4001 A/B | LIMIT SWITCH INDUCTIVE | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4167 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS417/P04 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 5 | - | 0 | - | 660UZSH4167 | - | LPG TO 660 G 4001 A/B | LIMIT SWITCH INDUCTIVE | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4167 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS417/P03 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 7 | - | 0 | - | 660PT4167 | - | LPG TO 660 G 4001 A/B - VALVE AIR RESERVE | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS/SIS | DCS | - | 0 | 10 |  | bar | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4167 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM401/P08 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 8 | - | 0 | - | 660PI4167 | - | LPG TO 660 G 4001 A/B | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4167 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 9 | - | 0 | - | 660PAL4167 | - | LPG TO 660 G 4001 A/B | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | 4.5 | bar | 214359C-6603-PID-0021-0407 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4167 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 1 | - | 0 | - | 660UVS4168 | - | Brine to LPG Dryer Recovery drum | ON OFF VALVE | - | - | - | - | - | L | - | BPCS/SIS | - | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4168 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIA | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 2 | - | 0 | - | 660UYS4168 | - | Brine to LPG Dryer Recovery drum | AIR SOLENOID SPRING | - | - | SOLENOID ONLY | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4168 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJCS421/C03-C04 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 3 | - | 0 | - | 660HLS4168 | - | Brine to LPG Dryer Recovery drum | TPL OPEN/CLOSE | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4168 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 4 | - | 0 | - | 660UZSL4168 | - | Brine to LPG Dryer Recovery drum | LIMIT SWITCH INDUCTIVE | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4168 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS416/P04 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 5 | - | 0 | - | 660UZSH4168 | - | Brine to LPG Dryer Recovery drum | LIMIT SWITCH INDUCTIVE | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4168 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS416/P03 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 7 | - | 0 | - | 660PT4168 | - | Brine to LPG Dryer Recovery drum - VALVE AIR RESERVE | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS/SIS | DCS | - | 0 | 10 |  | bar | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4168 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM409/P09 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 8 | - | 0 | - | 660PI4168 | - | Brine to LPG Dryer Recovery drum | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4168 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 9 | - | 0 | - | 660PAL4168 | - | Brine to LPG Dryer Recovery drum | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | 4.5 | bar | 214359C-6603-PID-0021-0408 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4168 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 1 | - | 0 | - | 660UVS4169 | - | FROM 660-D-4003 | ON OFF VALVE | - | - | - | - | - | L | - | BPCS/SIS | - | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4169 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 2 | - | 0 | - | 660UYS4169 | - | FROM 660-D-4003 | AIR SOLENOID SPRING | - | - | SOLENOID ONLY | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4169 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJCS418/C01-C02 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 3 | - | 0 | - | 660HLS4169 | - | FROM 660-D-4003 | TPL OPEN/CLOSE | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4169 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 4 | - | 0 | - | 660UZSL4169 | - | FROM 660-D-4003 | LIMIT SWITCH INDUCTIVE | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4169 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS417/P06 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 5 | - | 0 | - | 660UZSH4169 | - | FROM 660-D-4003 | LIMIT SWITCH INDUCTIVE | - | - | - | - | - | L | ST1D | BPCS/SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4169 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS417/P05 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 7 | - | 0 | - | 660PT4169 | - | FROM 660-D-4003 - VALVE AIR RESERVE | PRESSURE REL | - | - | - | - | - | L | ST1C | BPCS/SIS | DCS | - | 0 | 10 |  | bar | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4169 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI11 | INT | - | - | - | S | - | - | - | - | - | - | 660BJM401/P09 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 8 | - | 0 | - | 660PI4169 | - | FROM 660-D-4003 | INDICATION | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4169 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV10 | - | 9 | - | 0 | - | 660PAL4169 | - | FROM 660-D-4003 | ALARM | - | - | - | - | - | CRD | SdC | BPCS/SIS | DCS | - |  |  | 4.5 | bar | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4169 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 1 | - | 0 | - | 660UVS4170 | - | FROM 660-D-4003 | ON OFF VALVE | - | - | - | - | - | L | - | SIS | - | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4170 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | P | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 2 | - | 0 | - | 660UYS4170 | - | FROM 660-D-4003 | AIR SOLENOID SPRING | - | - | SOLENOID ONLY | - | - | L | ST1D | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4170 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJCS418/C13-C14 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 3 | - | 0 | - | 660HLS4170 | - | FROM 660-D-4003 | TPL OPEN/CLOSE | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4170 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 4 | - | 0 | - | 660UZSL4170 | - | FROM 660-D-4003 | LIMIT SWITCH INDUCTIVE | - | - | - | - | - | L | ST1D | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4170 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS417/P08 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV05 | - | 5 | - | 0 | - | 660UZSH4170 | - | FROM 660-D-4003 | LIMIT SWITCH INDUCTIVE | - | - | - | - | - | L | ST1D | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4170 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS417/P07 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV07 | - | 1 | - | 0 | - | 660UVS4222 | - | LP STEAM TO 660E4004 | ON OFF VALVE | - | - | - | - | - | L | - | SIS | - | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4222 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV07 | - | 2 | - | 0 | - | 660UYS4222 | - | LP STEAM TO 660E4004 | AIR SOLENOID SPRING | - | - | - | - | - | L | ST1D | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4222 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJCS414/C17-C18 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV07 | - | 3 | - | 0 | - | 660UZSH4222 | - | LP STEAM TO 660E4004 | LIMIT SWITCH | - | - | - | - | - | L | ST1D | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4222 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS412/P11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV07 | - | 4 | - | 0 | - | 660UZSL4222 | - | LP STEAM TO 660E4004 | LIMIT SWITCH | - | - | - | - | - | L | ST1D | SIS | S-PLC | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4222 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | 660BJMS412/P12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV07 | - | 5 | - | 0 | - | 660HLS4222 | - | LP STEAM TO 660E4004 | TPL OPEN/CLOSE | - | - | - | - | - | CRD | SdC | SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4222 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | UV07 | - | 7 | - | 0 | - | 660HS4222 | - | LP STEAM TO 660E4004 | PB SOFT | - | - | NORMALLY OPEN | - | - | CRD | SdC | SIS | DCS | - |  |  |  |  | 214359C-6603-PID-0021-0406 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4222 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660UY4510 | - | Solenoid Valve Nitrogen SVU 1 | AIR SOLENOID SPRING | - | - | - | - | - | L | ST1C | BPCS | DCS | - |  |  |  |  | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4510 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJC459/P1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660HS4510 | - | Solenoid Valve Nitrogen SVU 1 | PB SOFT | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4510 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660UY4511 | - | Solenoid Valve Nitrogen SVU 2 | AIR SOLENOID SPRING | - | - | - | - | - | L | ST1C | BPCS | DCS | - |  |  |  |  | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4511 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJC459/P2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660HS4511 | - | Solenoid Valve Nitrogen SVU 2 | PB SOFT | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4511 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660UY4512 | - | Solenoid Valve Nitrogen Clearance Pocket | AIR SOLENOID SPRING | - | - | - | - | - | L | ST1C | BPCS | DCS | - |  |  |  |  | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4512 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO11 | INT | - | - | - | R | - | - | - | - | - | - | 660BJC459/P3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660HS4512 | - | Solenoid Valve Nitrogen Clearance Pocket | PB SOFT | - | - | - | - | - | CRD | SdC | BPCS | DCS | - |  |  |  |  | 660-3-TENV-006001- 5 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660U4512 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660XL4407 | - | Local Control Panel Compressor | LIGHT | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660X4407 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | 660LP450 TB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660XL4408 | - | Local Control Panel Compressor | LIGHT | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660X4408 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | 660LP450 TB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660XL4409 | - | Local Control Panel Compressor | LIGHT | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660X4409 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | 660LP450 TB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660XL4410 | - | Local Control Panel Compressor | LIGHT | - | - | - | - | - | LP | ST1D | SIS | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660X4410 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DO10 | INT | - | - | - | R | - | - | - | - | - | - | 660LP450 TB1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660XTS4500 | - | Vibration Transmitter Crankcase NDE | ACCELEROMETER | - | - | - | - | - | L | ST1C | MAINT | MMS | - | 0 | 1250 |  | mm/s | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660X4500 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS458/P09 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660XSHH4500 | - | Vibration Transmitter Crankcase NDE | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1C | MAINT | MMS | - |  |  | 15 | mm/s | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660X4500 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660XAH4500 | - | Vibration Transmitter Crankcase NDE | ALARM | - | - | - | - | - | CRD | ST1C | MAINT | MMS | - |  |  | 12 | mm/s | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660X4500 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660XS4500 | - | Vibration Transmitter Crankcase NDE | CONTACT | - | - | NORMALLY CLOSE | - | - | ITR | ST1D | MAINT | S-PLC | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | FROM ST1C / MMS | - | - | - | - | 660X4500 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | DI10 | INT | - | - | - | R | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 8 | - | 0 | - | 660XTS4501 | - | Vibration Transmitter Crankcase NDE | ACCELEROMETER | - | - | - | - | - | L | ST1C | MAINT | MMS | - | 0 | 1250 |  | mm/s | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | MOTOR | - | - | - | - | 660X4501 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS458/P10 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 9 | - | 0 | - | 660XAH4501 | - | Vibration Transmitter Crankcase NDE | ALARM | - | - | - | - | - | CRD | ST1C | MAINT | MMS | - |  |  | 12 | mm/s | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660X4501 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 10 | - | 0 | - | 660XSHH4501 | - | Vibration Transmitter Crankcase NDE | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1C | MAINT | MMS | - |  |  | 15 | mm/s | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660X4501 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660XTS4502 | - | 660K4001-CROSSHEAD ACCELEROMETER | ACCELEROMETER | - | - | - | - | - | L | ST1C | MAINT | MMS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660X4502 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660XTS4503 | - | 660K4001-CROSSHEAD ACCELEROMETER | ACCELEROMETER | - | - | - | - | - | L | ST1C | MAINT | MMS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660X4503 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660XTS4504 | - | 660K4001-CROSSHEAD ACCELEROMETER | ACCELEROMETER | - | - | - | - | - | L | ST1C | MAINT | MMS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660X4504 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660XTS4505 | - | 660K4001-CROSSHEAD ACCELEROMETER | ACCELEROMETER | - | - | - | - | - | L | ST1C | MAINT | MMS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660X4505 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660XTS4506 | - | Vibration Transmitter Cylinder 2nd Stage | ACCELEROMETER | - | - | - | - | - | L | ST1C | MAINT | MMS | - | 0 | 500 |  | g | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660X4506 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS458/P11 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660XAH4506 | - | Vibration Transmitter Cylinder 2nd Stage | ALARM | - | - | - | - | - | CRD | ST1C | MAINT | MMS | - |  |  | 2.2 | g | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660X4506 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660XTS4507 | - | Vibration Transmitter Cylinder 1st Stage | ACCELEROMETER | - | - | - | - | - | L | ST1C | MAINT | MMS | - | 0 | 500 |  | g | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP | - | - | - | - | 660X4507 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS458/P12 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660XAH4507 | - | Vibration Transmitter Cylinder 1st Stage | ALARM | - | - | - | - | - | CRD | ST1C | MAINT | MMS | - |  |  | 2.2 | g | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660X4507 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 1 | - | 0 | - | 660XTS4508A | - | 660K4001-MOTOR BEARING RADIAL VIBRATION SENSOR (PROX | ACCELEROMETER | - | - | - | - | - | L | ST1C | MAINT | MMS | - | 0 | 1250 |  | mm/s | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | MOTOR | - | - | - | - | 660X4508 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS458/P13 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 2 | - | 0 | - | 660XTS4508B | - | 660K4001-MOTOR BEARING RADIAL VIBRATION SENSOR (PROX | ACCELEROMETER | - | - | - | - | - | L | ST1C | MAINT | MMS | - | 0 | 1250 |  | mm/s | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | MOTOR | - | - | - | - | 660X4508 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | AI20 | INT | - | - | - | - | - | - | - | - | - | - | 660BJIMS457/P18 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2 | IIC | T3 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 3 | - | 0 | - | 660XI4508A | - | 660K4001-MOTOR BEARING RADIAL VIBRATION SENSOR (PROX | INDICATION | - | - | - | - | - | CRD | ST1C | MAINT | MMS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660X4508 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 4 | - | 0 | - | 660XI4508B | - | 660K4001-MOTOR BEARING RADIAL VIBRATION SENSOR (PROX | INDICATION | - | - | - | - | - | CRD | ST1C | MAINT | MMS | - |  |  |  |  | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660X4508 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- | - | - | - | 5 | - | 0 | - | 660XSHH4508A | - | 660K4001-MOTOR BEARING RADIAL VIBRATION SENSOR (PROX | SOFT THRESHOLD | - | - | - | - | - | ITR | ST1C | MAINT | MMS | - |  |  | 7.1 | mm/s | 660-3-TENV-006001- 6 | - | - | - | - | 660-3-LPG Recovery | - | - | - | - | - | 660X4508 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
- |  | - |  | 6 | - | 0 | - | 660XSHH4508B | - | 660K4001-MOTOR BEARING RADIAL VIBRATION SENSOR (PROX | SOFT THRESHOLD |  |  | - |  |  | ITR | ST1C | MAINT | MMS |  |  |  | 7.1 | mm/s | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | - |  |  |  |  | 660X4508 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | - | - | - |  | - | - | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 7 | - | 0 | - | 660XAH4508 | - | 660K4001-MOTOR BEARING RADIAL VIBRATION SENSOR (PROX | ALARM |  |  | - |  |  | CRD | ST1C | MAINT | MMS |  |  |  | 4.5 | mm/s | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | - |  |  |  |  | 660X4508 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | - | - | - |  | - | - | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 8 | - | 0 | - | 660XS4508 | - | 660K4001-MOTOR BEARING RADIAL VIBRATION SENSOR (PROX | CONTACT |  |  | NORMALLY CLOSE |  |  | ITR | ST1D | MAINT | S-PLC | [5 empty] | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | FROM ST1C / MMS |  |  |  |  | 660X4508 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | DI10 | INT | - |  | - | R | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 1 | - | 0 |  | 660XTS4509A | - | 660K4001-MOTOR BEARING RADIAL VIBRATION SENSOR (PROX | ACCELEROMETER |  |  | - |  |  | L | ST1C | MAINT | MMS |  | 0 | 1250 |  | mm/s | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | MOTOR |  |  |  |  | 660X4509 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | AI20 | INT | - |  | - | - | [6 empty] | 660BJIMS458/P14 |  |  |  |  | - | [21 empty] | - | 2 | IIC | T3 | [37 empty] | - | -
- |  | - |  | 2 | - | 0 | - | 660XTS4509B | - | 660K4001-MOTOR BEARING RADIAL VIBRATION SENSOR (PROX | ACCELEROMETER |  |  | - |  |  | L | ST1C | MAINT | MMS |  | 0 | 1250 |  | mm/s | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | MOTOR |  |  |  |  | 660X4509 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | AI20 | INT | - |  | - | - | [6 empty] | 660BJIMS457/P19 |  |  |  |  | - | [21 empty] | - | 2 | IIC | T3 | [37 empty] | - | -
- |  | - |  | 3 | - | 0 | - | 660XI4509A | - | 660K4001-MOTOR BEARING RADIAL VIBRATION SENSOR (PROX | INDICATION |  |  | - |  |  | CRD | ST1C | MAINT | MMS | [5 empty] | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | - |  |  |  |  | 660X4509 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | - | - | - |  | - | - | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 4 | - | 0 | - | 660XI4509B | - | 660K4001-MOTOR BEARING RADIAL VIBRATION SENSOR (PROX | INDICATION |  |  | - |  |  | CRD | ST1C | MAINT | MMS | [5 empty] | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | - |  |  |  |  | 660X4509 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | - | - | - |  | - | - | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 5 | - | 0 | - | 660XSHH4509A | - | 660K4001-MOTOR BEARING RADIAL VIBRATION SENSOR (PROX | SOFT THRESHOLD |  |  | - |  |  | ITR | ST1C | MAINT | MMS |  |  |  | 7.1 | mm/s | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | - |  |  |  |  | 660X4509 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | - | - | - |  | - | - | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 6 | - | 0 | - | 660XSHH4509B | - | 660K4001-MOTOR BEARING RADIAL VIBRATION SENSOR (PROX | SOFT THRESHOLD |  |  | - |  |  | ITR | ST1C | MAINT | MMS |  |  |  | 7.1 | mm/s | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | - |  |  |  |  | 660X4509 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | - | - | - |  | - | - | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 7 | - | 0 | - | 660XAH4509 | - | 660K4001-MOTOR BEARING RADIAL VIBRATION SENSOR (PROX | ALARM |  |  | - |  |  | CRD | ST1C | MAINT | MMS |  |  |  | 4.5 | mm/s | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | - |  |  |  |  | 660X4509 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | - | - | - |  | - | - | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 8 | - | 0 | - | 660XS4509 | - | 660K4001-MOTOR BEARING RADIAL VIBRATION SENSOR (PROX | CONTACT |  |  | NORMALLY CLOSE |  |  | ITR | ST1D | MAINT | S-PLC | [5 empty] | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | FROM ST1C / MMS |  |  |  |  | 660X4509 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | DI10 | INT | - |  | - | R | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 7 | - | 0 |  | 660XAH4510 | - | 660K4001-FRAME RADIAL VIBRATION ACCELEROMETER | ALARM |  |  | - |  |  | CRD | ST1C | MAINT | MMS |  |  |  | 0.92 | g | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | - |  |  |  |  | 660X4510 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | - | - | - |  | - | - | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 8 | - | 0 |  | 660XI4510A | - | 660K4001-FRAME RADIAL VIBRATION ACCELEROMETER | INDICATION |  |  | - |  |  | CRD | ST1C | MAINT | MMS | [5 empty] | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | - |  |  |  |  | 660X4510 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | - | - | - |  | - | - | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 9 | - | 0 |  | 660XI4510B | - | 660K4001-FRAME RADIAL VIBRATION ACCELEROMETER | INDICATION |  |  | - |  |  | CRD | ST1C | MAINT | MMS | [5 empty] | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | - |  |  |  |  | 660X4510 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | - | - | - |  | - | - | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 10 | - | 0 |  | 660XSHH4510A | - | 660K4001-FRAME RADIAL VIBRATION ACCELEROMETER | SOFT THRESHOLD |  |  | - |  |  | ITR | ST1C | MAINT | MMS |  |  |  | 1.33 | g | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | - |  |  |  |  | 660X4510 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | - | - | - |  | - | - | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 11 | - | 0 |  | 660XSHH4510B | - | 660K4001-FRAME RADIAL VIBRATION ACCELEROMETER | SOFT THRESHOLD |  |  | - |  |  | ITR | ST1C | MAINT | MMS |  |  |  | 1.33 | g | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | - |  |  |  |  | 660X4510 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | - | - | - |  | - | - | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 12 | - | 0 |  | 660XTS4510A | - | 660K4001-FRAME RADIAL VIBRATION ACCELEROMETER | ACCELEROMETER |  |  | - |  |  | L | ST1C | MAINT | MMS |  | 0 | 50 |  | g | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP |  |  |  |  | 660X4510 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | AI20 | INT | - |  | - | - | [6 empty] | 660BJIMS458/P15 |  |  |  |  | - | [21 empty] | - | 2 | IIC | T3 | [37 empty] | - | -
- |  | - |  | 13 | - | 0 |  | 660XTS4510B | - | 660K4001-FRAME RADIAL VIBRATION ACCELEROMETER | ACCELEROMETER |  |  | - |  |  | L | ST1C | MAINT | MMS |  | 0 | 50 |  | g | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP |  |  |  |  | 660X4510 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | AI20 | INT | - |  | - | - | [6 empty] | 660BJIMS458/P16 |  |  |  |  | - | [21 empty] | - | 2 | IIC | T3 | [37 empty] | - | -
- |  | - |  | 14 | - | 0 | - | 660XS4510 | - | 660K4001-FRAME RADIAL VIBRATION ACCELEROMETER | CONTACT |  |  | NORMALLY CLOSE |  |  | ITR | ST1D | MAINT | S-PLC | [5 empty] | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | FROM ST1C / MMS |  |  |  |  | 660X4510 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | DI10 | INT | - |  | - | R | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 1 | - | 0 |  | 660XTS4511A | - | 660K4001-MOTOR BEARING RADIAL VIBRATION SENSOR (PROX | ACCELEROMETER |  |  | - |  |  | L | ST1C | MAINT | MMS |  | 0 | 50 |  | g | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | MOTOR |  |  |  |  | 660X4511 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | AI20 | INT | - |  | - | - | [6 empty] | 660BJIMS458/P17 |  |  |  |  | - | [21 empty] | - | 2 | IIC | T3 | [37 empty] | - | -
- |  | - |  | 2 | - | 0 | - | 660XTS4511B | - | 660K4001-MOTOR BEARING RADIAL VIBRATION SENSOR (PROX | ACCELEROMETER |  |  | - |  |  | L | ST1C | MAINT | MMS |  | 0 | 50 |  | g | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | MOTOR |  |  |  |  | 660X4511 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | AI20 | INT | - |  | - | - | [6 empty] | 660BJIMS458/P18 |  |  |  |  | - | [21 empty] | - | 2 | IIC | T3 | [37 empty] | - | -
- |  | - |  | 3 | - | 0 | - | 660XI4511A | - | 660K4001-MOTOR BEARING RADIAL VIBRATION SENSOR (PROX | INDICATION |  |  | - |  |  | CRD | ST1C | MAINT | MMS | [5 empty] | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | - |  |  |  |  | 660X4511 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | - | - | - |  | - | - | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 4 | - | 0 | - | 660XI4511B | - | 660K4001-MOTOR BEARING RADIAL VIBRATION SENSOR (PROX | INDICATION |  |  | - |  |  | CRD | ST1C | MAINT | MMS | [5 empty] | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | - |  |  |  |  | 660X4511 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | - | - | - |  | - | - | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 5 | - | 0 | - | 660XAH4511 | - | 660K4001-MOTOR BEARING RADIAL VIBRATION SENSOR (PROX | ALARM |  |  | - |  |  | CRD | ST1C | MAINT | MMS |  |  |  | 0.92 | g | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | - |  |  |  |  | 660X4511 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | - | - | - |  | - | - | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 6 | - | 0 | - | 660XSHH4511A | - | 660K4001-MOTOR BEARING RADIAL VIBRATION SENSOR (PROX | SOFT THRESHOLD |  |  | - |  |  | ITR | ST1C | MAINT | MMS |  |  |  | 1.33 | g | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | - |  |  |  |  | 660X4511 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | - | - | - |  | - | - | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 7 | - | 0 | - | 660XSHH4511B | - | 660K4001-MOTOR BEARING RADIAL VIBRATION SENSOR (PROX | SOFT THRESHOLD |  |  | - |  |  | ITR | ST1C | MAINT | MMS |  |  |  | 1.33 | g | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | - |  |  |  |  | 660X4511 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | - | - | - |  | - | - | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 8 | - | 0 | - | 660XS4511 | - | 660K4001-MOTOR BEARING RADIAL VIBRATION SENSOR (PROX | CONTACT |  |  | NORMALLY CLOSE |  |  | ITR | ST1D | MAINT | S-PLC | [5 empty] | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | FROM ST1C / MMS |  |  |  |  | 660X4511 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | DI10 | INT | - |  | - | R | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 1 | - | 0 | - | 660XTS4512 | - | 660K4001-MOTOR BEARING RADIAL VIBRATION SENSOR (ACCE | ACCELEROMETER |  |  | - |  |  | L | ST1C | MAINT | MMS | [5 empty] | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | MOTOR |  |  |  |  | 660X4512 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | AI20 | INT | - |  | - | - | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 1 | - | 0 | - | 660XTS4513 | - | 660K4001-MOTOR BEARING RADIAL VIBRATION SENSOR (ACCE | ACCELEROMETER |  |  | - |  |  | L | ST1C | MAINT | MMS | [5 empty] | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | MOTOR |  |  |  |  | 660X4513 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | AI20 | INT | - |  | - | - | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 1 | - | 0 | - | 660XTS4514 | - | 660K4001-MOTOR BEARING RADIAL VIBRATION SENSOR (ACCE | ACCELEROMETER |  |  | - |  |  | L | ST1C | MAINT | MMS | [5 empty] | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | MOTOR |  |  |  |  | 660X4514 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | AI20 | INT | - |  | - | - | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 1 | - | 0 | - | 660XTS4515 | - | 660K4001-MOTOR BEARING RADIAL VIBRATION SENSOR (ACCE | ACCELEROMETER |  |  | - |  |  | L | ST1C | MAINT | MMS | [5 empty] | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | MOTOR |  |  |  |  | 660X4515 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | AI20 | INT | - |  | - | - | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 1 | - | 0 |  | 660XS4520 | - | 660 K 4001 MPS RACK ON | CONTACT |  |  | - |  |  | ITR | ST1D | MAINT | S-PLC | [5 empty] | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | - |  |  |  |  | 660X4520 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | DI10 | INT | - |  | - | R | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 1 | - | 0 | - | 660XS4521 | - | 660 K 4001 MPS GENERAL ALARM | CONTACT |  |  | - |  |  | ITR | ST1D | MAINT | S-PLC | [5 empty] | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | - |  |  |  |  | 660X4521 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | DI10 | INT | - |  | - | R | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 1 | - | 0 | - | 660XS4550 | - | 660K4001 TRIP FROM MPS TO S-PLC | CONTACT |  |  | NORMALLY CLOSE |  |  | ITR | ST1D | MAINT | S-PLC | [5 empty] | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | FROM ST1C / MMS |  |  |  |  | 660X4550 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | DI10 | INT | - |  | - | R | [6 empty] | N/A |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 1 | - | 0 | - | 660XS4551 | - | 660K4001 TRIP FROM MPS TO S-PLC | CONTACT |  |  | NORMALLY CLOSE |  |  | ITR | ST1D | MAINT | S-PLC | [5 empty] | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | FROM ST1C / MMS |  |  |  |  | 660X4551 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | DI10 | INT | - |  | - | R | [6 empty] | N/A |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 1 | - | 0 | - | 660XS4552 | - | 660K4001 TRIP FROM MPS TO S-PLC | CONTACT |  |  | NORMALLY CLOSE |  |  | ITR | ST1D | MAINT | S-PLC | [5 empty] | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | FROM ST1C / MMS |  |  |  |  | 660X4552 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | DI10 | INT | - |  | - | R | [6 empty] | N/A |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 1 | - | 0 | - | 660XS4553 | - | 660K4001 TRIP FROM MPS TO S-PLC | CONTACT |  |  | NORMALLY CLOSE |  |  | ITR | ST1D | MAINT | S-PLC | [5 empty] | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | FROM ST1C / MMS |  |  |  |  | 660X4553 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | DI10 | INT | - |  | - | R | [6 empty] | N/A |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 1 | - | 0 | - | 660XS4554 | - | 660K4001 TRIP FROM MPS TO S-PLC | CONTACT |  |  | NORMALLY CLOSE |  |  | ITR | ST1D | MAINT | S-PLC | [5 empty] | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | FROM ST1C / MMS |  |  |  |  | 660X4554 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | DI10 | INT | - |  | - | R | [6 empty] | N/A |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 1 | - | 0 | - | 660XS4555 | - | 660K4001 TRIP FROM MPS TO S-PLC | CONTACT |  |  | NORMALLY CLOSE |  |  | ITR | ST1D | MAINT | S-PLC | [5 empty] | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | FROM ST1C / MMS |  |  |  |  | 660X4555 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | DI10 | INT | - |  | - | R | [6 empty] | N/A |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 1 | - | 0 | - | 660XS4556 | - | 660K4001 TRIP FROM MPS TO S-PLC | CONTACT |  |  | NORMALLY CLOSE |  |  | ITR | ST1D | MAINT | S-PLC | [5 empty] | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | FROM ST1C / MMS |  |  |  |  | 660X4556 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | DI10 | INT | - |  | - | R | [6 empty] | N/A |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 1 | - | 0 | - | 660XS4557 | - | 660K4001 TRIP FROM MPS TO S-PLC | CONTACT |  |  | NORMALLY CLOSE |  |  | ITR | ST1D | MAINT | S-PLC | [5 empty] | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | FROM ST1C / MMS |  |  |  |  | 660X4557 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | DI10 | INT | - |  | - | R | [6 empty] | N/A |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 1 | - | 0 | - | 660ZT4500 | - | 660K4001-AXIAL DISPLACEMENT SENSOR (PROXIMITOR) | AXIAL DISPLACEMEN |  |  | - |  |  | L | ST1C | MAINT | MMS |  | 0.25 | 2.25 |  | mm | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP |  |  |  |  | 660Z4500 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | AI20 | INT | - |  | - | - | [6 empty] | 660BJIMS458/P03-02 |  |  |  |  | - | [21 empty] | - | 2 | IIC | T3 | [37 empty] | - | -
- |  | - |  | 2 | - | 0 | - | 660ZI4500 | - | 660K4001-AXIAL DISPLACEMENT SENSOR (PROXIMITOR) | INDICATION |  |  | - |  |  | CRD | ST1C | MAINT | MMS | [5 empty] | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | - |  |  |  |  | 660Z4500 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | - | - | - |  | - | - | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 3 | - | 0 | - | 660ZAH4500 | - | 660K4001-AXIAL DISPLACEMENT SENSOR (PROXIMITOR) | ALARM |  |  | - |  |  | CRD | ST1C | MAINT | MMS |  |  |  | 1.6029 | mm | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | - |  |  |  |  | 660Z4500 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | - | - | - |  | - | - | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 4 | - | 0 | - | 660ZSHH4500 | - | 660K4001-AXIAL DISPLACEMENT SENSOR (PROXIMITOR) | SOFT THRESHOLD |  |  | - |  |  | ITR | ST1C | MAINT | MMS |  |  |  | 1.6783 | mm | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | - |  |  |  |  | 660Z4500 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | - | - | - |  | - | - | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 5 | - | 0 | - | 660ZS4500 | - | 660K4001-AXIAL DISPLACEMENT SENSOR (PROXIMITOR) | CONTACT |  |  | NORMALLY CLOSE |  |  | ITR | ST1D | MAINT | S-PLC | [5 empty] | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | FROM ST1C / MMS |  |  |  |  | 660Z4500 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | DI10 | INT | - |  | - | R | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 1 | - | 0 | - | 660ZT4501 | - | 660K4001-AXIAL DISPLACEMENT SENSOR (PROXIMITOR) | AXIAL DISPLACEMEN |  |  | - |  |  | L | ST1C | MAINT | MMS |  | 0.25 | 2.25 |  | mm | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP |  |  |  |  | 660Z4501 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | AI20 | INT | - |  | - | - | [6 empty] | 660BJIMS458/P01-02 |  |  |  |  | - | [21 empty] | - | 2 | IIC | T3 | [37 empty] | - | -
- |  | - |  | 2 | - | 0 | - | 660ZI4501 | - | 660K4001-AXIAL DISPLACEMENT SENSOR (PROXIMITOR) | INDICATION |  |  | - |  |  | CRD | ST1C | MAINT | MMS | [5 empty] | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | - |  |  |  |  | 660Z4501 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | - | - | - |  | - | - | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 3 | - | 0 | - | 660ZAH4501 | - | 660K4001-AXIAL DISPLACEMENT SENSOR (PROXIMITOR) | ALARM |  |  | - |  |  | CRD | ST1C | MAINT | MMS |  |  |  | 1.7487 | mm | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | - |  |  |  |  | 660Z4501 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | - | - | - |  | - | - | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 4 | - | 0 | - | 660ZSHH4501 | - | 660K4001-AXIAL DISPLACEMENT SENSOR (PROXIMITOR) | SOFT THRESHOLD |  |  | - |  |  | ITR | ST1C | MAINT | MMS |  |  |  | 1.8424 | mm | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | - |  |  |  |  | 660Z4501 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | - | - | - |  | - | - | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 5 | - | 0 | - | 660ZS4501 | - | 660K4001-AXIAL DISPLACEMENT SENSOR (PROXIMITOR) | CONTACT |  |  | NORMALLY CLOSE |  |  | ITR | ST1D | MAINT | S-PLC | [5 empty] | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | FROM ST1C / MMS |  |  |  |  | 660Z4501 | N | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | DI10 | INT | - |  | - | R | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 1 | - | 0 | - | 660ZT4502 | - | 660K4001-AXIAL DISPLACEMENT SENSOR (PROXIMITOR) | AXIAL DISPLACEMEN |  |  | - |  |  | L | ST1C | MAINT | MMS | [5 empty] | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP |  |  |  |  | 660Z4502 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | AI20 | INT | - |  | - | - | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 1 | - | 0 | - | 660ZT4503 | - | 660K4001-AXIAL DISPLACEMENT SENSOR (PROXIMITOR) | AXIAL DISPLACEMEN |  |  | - |  |  | L | ST1C | MAINT | MMS | [5 empty] | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP |  |  |  |  | 660Z4503 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | AI20 | INT | - |  | - | - | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 1 | - | 0 | - | 660ZT4504 | - | 660K4001-AXIAL DISPLACEMENT SENSOR (PROXIMITOR) | AXIAL DISPLACEMEN |  |  | - |  |  | L | ST1C | MAINT | MMS | [5 empty] | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP |  |  |  |  | 660Z4504 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | AI20 | INT | - |  | - | - | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 1 | - | 0 | - | 660ZT4505 | - | 660K4001-AXIAL DISPLACEMENT SENSOR (PROXIMITOR) | AXIAL DISPLACEMEN |  |  | - |  |  | L | ST1C | MAINT | MMS | [5 empty] | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP |  |  |  |  | 660Z4505 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | AI20 | INT | - |  | - | - | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 1 | - | 0 | - | 660ZT4506 | - | 660K4001-PISTON ROD DROP PROXIMITY SENSOR | AXIAL DISPLACEMEN |  |  | - |  |  | L | ST1C | MAINT | MMS | [5 empty] | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP |  |  |  |  | 660Z4506 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | AI20 | INT | - |  | - | - | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 1 | - | 0 | - | 660ZT4507 | - | 660K4001-PISTON ROD DROP PROXIMITY SENSOR | AXIAL DISPLACEMEN |  |  | - |  |  | L | ST1C | MAINT | MMS | [5 empty] | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | RECIP/SCEW COMP |  |  |  |  | 660Z4507 | C | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | AI20 | INT | - |  | - | - | [6 empty] | - |  |  |  |  | - | [21 empty] | - | - | - | - | [37 empty] | - | -
- |  | - |  | 1 | - | 0 | - | 660ZTS4508 | - | 660K4001-KEYPHASOR | KEYPHASOR |  |  | - |  |  | L | ST1C | MAINT | MMS |  | 0 | 1500 |  | Hz | 660-3-TENV-006001- 6 |  | - | - | - | 660-3-LPG Recovery | - |  |  |  |  | 660Z4508 | NbO2 | - | - | - | - | - | - | - | - | - | - | - | - | - | [35 empty] | AI20 | INT | - |  | - | - | [6 empty] | 660BJIMS458/P04 |  |  |  |  | - | [21 empty] | - | 2 | IIC | T3 | [37 empty] | - | -
Note on W7: Joan Bofill-Cardona: This data will be updated automatically when the SP is done. For Speed control range shall be manually.
Note on X7: Joan Bofill-Cardona: This data will be updated automatically when the SP is done. For Speed control range shall be manually.
Note on AL7: Joan Bofill-Cardona: This data will be updated automatically when the SP is done
Note on BY7: Joan Bofill-Cardona: Instrument range (All Span)
Note on BZ7: Joan Bofill-Cardona: Instrument range (All Span)
Note on CB7: Joan Bofill-Cardona: Calibration of Instrument
Note on CC7: Joan Bofill-Cardona: Calibration of Instrument
Note on FL9: Paulo-Gilberto Martins-Afonso-External: 0 Meaning
Note on FM9: Paulo-Gilberto Martins-Afonso-External: 0 Meaning
Note on FN9: Paulo-Gilberto Martins-Afonso-External: 0 Meaning
Note on FO9: Paulo-Gilberto Martins-Afonso-External: 0 Meaning